## Emission Limits
Industrial Emissions Directive - 2010/75/EU
Notes
Two types of combustion plants, defined in Article 30
Article 30(2) - Combustion plants which have been granted a permit before 7 January 2013, or the operators have submitted a complete application for a permit before that date, and in operation no later tha 7 January 2014
Article 30(3) - combustion plants not covered by article 30(3)
Gas turbines and gas engines for emergency use that operate for less than 500 operating hours per year are not covered by the emission limit values set out in this point.
IED Emission Limit Values
Fuel | Type of plant | Min Rated Thermal Input (MW) | Max Rated Thermal Input (MW) | NOx (mg/Nm3) | Type of Plant | Permit granted (before) | Permit granted (after) | Notes
Coal and lignite and other solid fuels |  | 50 | 100 | 300 | Article 30(2) | 2013-01-07
Pulverised lignite |  | 50 | 100 | 450 | Article 30(2) | 2013-01-07
Biomass |  | 50 | 100 | 300 | Article 30(2) | 2013-01-07
Peat |  | 50 | 100 | 300 | Article 30(2) | 2013-01-07
Liquid fuels |  | 50 | 100 | 450 | Article 30(2) | 2013-01-07
Coal and lignite and other solid fuels |  | 100 | 300 | 200 | Article 30(2) | 2013-01-07
Biomass |  | 100 | 300 | 250 | Article 30(2) | 2013-01-07
Peat |  | 100 | 300 | 250 | Article 30(2) | 2013-01-07
Liquid fuels |  | 100 | 300 | 200 | Article 30(2) | 2013-01-07
Liquid fuels - refining crude oil |  | 100 | 500 | 450 | Article 30(2) | 2002-11-27 |  | The emission limit value is 450 mg/Nm3 for the firing of distillation and conversion residues from the refining of crude-oil for own consumption in combustion plants
Coal and lignite and other solid fuels |  | 300 |  | 200 | Article 30(2) | 2013-01-07
Biomass |  | 300 |  | 200 | Article 30(2) | 2013-01-07
Peat |  | 300 |  | 200 | Article 30(2) | 2013-01-07
Liquid fuels |  | 300 |  | 150 | Article 30(2) | 2013-01-07
Liquid production residues |  | 1 | 500 | 450 | Article 30(2) | 2002-11-27 |  | For own consumption.
Solid or liquid fuels |  | 1 | 500 | 450 | Article 30(2) | 2002-11-27 |  | Plants that do not operate for more than 1500 hours per year as a rolling average over a period of 5 years
Solid fuels |  | 500 |  | 450 | Article 30(2) | 1987-07-01 |  | Plants that do not operate for more than 1500 hours per year as a rolling average over a period of 5 years
Liquid fuels |  | 500 |  | 400 | Article 30(2) | 2002-11-27 |  | Plants that do not operate for more than 1500 hours per year as a rolling average over a period of 5 years
Gas | Natural gas with the exception of gas turbines and gas engines | 50 |  | 100 | Article 30(2) | 2013-01-07
Gas | Blast furnace gas, coke oven gas, or low calorific gases from gasification of refinery residues with the exception of gas turbines and gas engines | 50 |  | 200 | Article 30(2) | 2013-01-07
Gas | Blast furnace gas, coke oven gas, or low calorific gases from gasification of refinery residues with the exception of gas turbines and gas engines | 50 | 500 | 300 | Article 30(2) | 2002-11-27
Gas | Other gases with the exception of gas turbines and gas engines | 50 |  | 200 | Article 30(2) | 2013-01-07
Gas | Other gases with the exception of gas turbines and gas engines | 50 | 500 | 300 | Article 30(2) | 2002-11-27
Gas | Gas turbines (including CCGT) using natural gas as fuel | 50 |  | 50 | Article 30(2) | 2013-01-07 |  | Apply only above 70% load
Gas | Gas turbines (including CCGT) using natural gas as fuel | 50 |  | 75 | Article 30(2) | 2013-01-07 |  | Apply only above 70% load, For gas turbines used in combines heat and power systems and having an overall efficiency greater than 75%
Gas | Gas turbines (including CCGT) using natural gas as fuel | 50 |  | 75 | Article 30(2) | 2013-01-07 |  | Apply only above 70% load, For gas turbines used in combined cycle plants having an annual overall efficiency greater than 55%
Gas | Gas turbines (including CCGT) using natural gas as fuel | 50 |  | 75 | Article 30(2) | 2013-01-07 |  | Apply only above 70% load, Gas turbines for mechanical drives
Gas | Gas turbines (including CCGT) using natural gas as fuel | 50 |  | 150 | Article 30(2) | 2013-01-07 |  | Plants that do not operate for more than 1500 hours per year as a rolling average over a period of 5 years
Gas | Gas turbines (including CCGT) using other gases as fuel | 50 |  | 120 | Article 30(2) | 2013-01-07 |  | Apply only above 70% load
Gas | Gas turbines (including CCGT) using other gases as fuel | 50 |  | 200 | Article 30(2) | 2002-11-27 |  | Plants that do not operate for more than 1500 hours per year as a rolling average over a period of 5 years
Gas | Gas engines | 50 |  | 100 | Article 30(2) | 2013-01-07
Coal and lignite and other solid fuels |  | 50 | 100 | 300 | Article 30(3) |  | 2013-01-08
Pulverised lignite |  | 50 | 100 | 400 | Article 30(3) |  | 2013-01-08
Biomass |  | 50 | 100 | 250 | Article 30(3) |  | 2013-01-08
Peat |  | 50 | 100 | 250 | Article 30(3) |  | 2013-01-08
Liquid fuels |  | 50 | 100 | 300 | Article 30(3) |  | 2013-01-08
Coal and lignite and other solid fuels |  | 100 | 300 | 200 | Article 30(3) |  | 2013-01-08
Biomass |  | 100 | 300 | 200 | Article 30(3) |  | 2013-01-08
Peat |  | 100 | 300 | 200 | Article 30(3) |  | 2013-01-08
Liquid fuels |  | 100 | 300 | 150 | Article 30(3) |  | 2013-01-08
Coal and lignite and other solid fuels |  | 300 |  | 150 | Article 30(3) |  | 2013-01-08
Pulverised lignite |  | 300 |  | 200 | Article 30(3) |  | 2013-01-08
Biomass |  | 300 |  | 150 | Article 30(3) |  | 2013-01-08
Peat |  | 300 |  | 150 | Article 30(3) |  | 2013-01-08
Liquid fuels |  | 300 |  | 100 | Article 30(3) |  | 2013-01-08
Liquid fuels - light and middle distillates | Gas turbines (including CCGT) | 50 |  | 50 | Article 30(3) |  | 2013-01-08
Gas | Combustion plants other than gas turbines and gas engines | 50 |  | 100 | Article 30(3) |  | 2013-01-08 | Apply only above 70% load. For single cycle gas turbines having an efficiency greater than 35 % – determined at ISO base load conditions – the emission limit value for NOx shall be 50xη/35 where η is the gas turbine efficiency at ISO base load conditions expressed as a percentage.
Gas | Gas turbines (including CCGT) | 50 |  | 50 | Article 30(3) |  | 2013-01-08 | Apply only above 70% load. For single cycle gas turbines having an efficiency greater than 35 % – determined at ISO base load conditions – the emission limit value for NOx shall be 50xη/35 where η is the gas turbine efficiency at ISO base load conditions expressed as a percentage.
Gas | Gas engines | 50 |  | 75 | Article 30(3) |  | 2013-01-08

## converted_EFs
Fuel | Type of plant | Min Rated Thermal Input (MW) | Max Rated Thermal Input (MW) | Midpoint | NOx (mg/Nm3) | NOx g/kWh (net thermal) |  | Type of Plant | Permit granted (before) | Permit granted (after) | Conversion factors
[7 empty] | NOx g/kWh (output) |  |  |  | Coal | 767
Coal and lignite and other solid fuels |  | 50 | 100 | 75 | 300 | 0.39113 | 0.65189 | Article 30(2) | 2013-01-07 |  | Gas | 980
Pulverised lignite |  | 50 | 100 | 75 | 450 | 0.5867 | 0.97784 | Article 30(2) | 2013-01-07 |  | Oil | 983
Biomass |  | 50 | 100 | 75 | 300 | 0.41667 | 0.69444 | Article 30(2) | 2013-01-07 |  | Wood | 720
Peat |  | 50 | 100 | 75 | 300 | - |  | Article 30(2) | 2013-01-07
Liquid fuels |  | 50 | 100 | 75 | 450 | - |  | Article 30(2) | 2013-01-07
Coal and lignite and other solid fuels |  | 100 | 300 | 200 | 200 | 0.26076 | 0.43459 | Article 30(2) | 2013-01-07
Biomass |  | 100 | 300 | 200 | 250 | 0.34722 | 0.5787 | Article 30(2) | 2013-01-07
Peat |  | 100 | 300 | 200 | 250 |  |  | Article 30(2) | 2013-01-07
Liquid fuels |  | 100 | 300 | 200 | 200 |  |  | Article 30(2) | 2013-01-07
Liquid fuels - refining crude oil |  | 100 | 500 | 300 | 450 |  |  | Article 30(2) | 2002-11-27
Coal and lignite and other solid fuels |  | 300 |  | 300 | 200 | 0.26076 | 0.43459 | Article 30(2) | 2013-01-07
Biomass |  | 300 |  | 300 | 200 | 0.27778 | 0.46296 | Article 30(2) | 2013-01-07
Peat |  | 300 |  | 300 | 200 |  |  | Article 30(2) | 2013-01-07
Liquid fuels |  | 300 |  | 300 | 150 |  |  | Article 30(2) | 2013-01-07
Liquid production residues |  | 1 | 500 | 250.5 | 450 |  |  | Article 30(2) | 2002-11-27
Solid or liquid fuels |  | 1 | 500 | 250.5 | 450 |  |  | Article 30(2) | 2002-11-27
Solid fuels |  | 500 |  | 500 | 450 |  |  | Article 30(2) | 1987-07-01
Liquid fuels |  | 500 |  | 500 | 400 |  |  | Article 30(2) | 2002-11-27
Gas | Natural gas with the exception of gas turbines and gas engines | 50 |  | 50 | 100 | 0.10204 | 0.17007 | Article 30(2) | 2013-01-07
Gas | Blast furnace gas, coke oven gas, or low calorific gases from gasification of refinery residues with the exception of gas turbines and gas engines | 50 |  | 50 | 200 | 0.20408 | 0.34014 | Article 30(2) | 2013-01-07
Gas | Blast furnace gas, coke oven gas, or low calorific gases from gasification of refinery residues with the exception of gas turbines and gas engines | 50 | 500 | 275 | 300 | 0.30612 | 0.5102 | Article 30(2) | 2002-11-27
Gas | Other gases with the exception of gas turbines and gas engines | 50 |  | 50 | 200 | 0.20408 | 0.34014 | Article 30(2) | 2013-01-07
Gas | Other gases with the exception of gas turbines and gas engines | 50 | 500 | 275 | 300 | 0.30612 | 0.5102 | Article 30(2) | 2002-11-27
Gas | Gas turbines (including CCGT) using natural gas as fuel | 50 |  | 50 | 50 | 0.05102 | 0.085034 | Article 30(2) | 2013-01-07
Gas | Gas turbines (including CCGT) using natural gas as fuel | 50 |  | 50 | 75 | 0.076531 | 0.12755 | Article 30(2) | 2013-01-07
Gas | Gas turbines (including CCGT) using natural gas as fuel | 50 |  | 50 | 75 | 0.076531 | 0.12755 | Article 30(2) | 2013-01-07
Gas | Gas turbines (including CCGT) using natural gas as fuel | 50 |  | 50 | 75 | 0.076531 | 0.12755 | Article 30(2) | 2013-01-07
Gas | Gas turbines (including CCGT) using natural gas as fuel | 50 |  | 50 | 150 | 0.15306 | 0.2551 | Article 30(2) | 2013-01-07
Gas | Gas turbines (including CCGT) using other gases as fuel | 50 |  | 50 | 120 | 0.12245 | 0.20408 | Article 30(2) | 2013-01-07
Gas | Gas turbines (including CCGT) using other gases as fuel | 50 |  | 50 | 200 | 0.20408 | 0.34014 | Article 30(2) | 2002-11-27
Gas | Gas engines | 50 |  | 50 | 100 | 0.10204 | 0.17007 | Article 30(2) | 2013-01-07
Coal and lignite and other solid fuels |  | 50 | 100 | 75 | 300 | 0.39113 | 0.65189 | Article 30(3) |  | 2013-01-08
Pulverised lignite |  | 50 | 100 | 75 | 400 | 0.52151 | 0.86919 | Article 30(3) |  | 2013-01-08
Biomass |  | 50 | 100 | 75 | 250 | 0.34722 | 0.5787 | Article 30(3) |  | 2013-01-08
Peat |  | 50 | 100 | 75 | 250 |  |  | Article 30(3) |  | 2013-01-08
Liquid fuels |  | 50 | 100 | 75 | 300 |  |  | Article 30(3) |  | 2013-01-08
Coal and lignite and other solid fuels |  | 100 | 300 | 200 | 200 | 0.26076 | 0.43459 | Article 30(3) |  | 2013-01-08
Biomass |  | 100 | 300 | 200 | 200 | 0.27778 | 0.46296 | Article 30(3) |  | 2013-01-08
Peat |  | 100 | 300 | 200 | 200 |  |  | Article 30(3) |  | 2013-01-08
Liquid fuels |  | 100 | 300 | 200 | 150 |  |  | Article 30(3) |  | 2013-01-08
Coal and lignite and other solid fuels |  | 300 |  | 300 | 150 | 0.19557 | 0.32595 | Article 30(3) |  | 2013-01-08
Pulverised lignite |  | 300 |  | 300 | 200 | 0.26076 | 0.43459 | Article 30(3) |  | 2013-01-08
Biomass |  | 300 |  | 300 | 150 | 0.20833 | 0.34722 | Article 30(3) |  | 2013-01-08
Peat |  | 300 |  | 300 | 150 |  |  | Article 30(3) |  | 2013-01-08
Liquid fuels |  | 300 |  | 300 | 100 |  |  | Article 30(3) |  | 2013-01-08
Liquid fuels - light and middle distillates | Gas turbines (including CCGT) | 50 |  | 50 | 50 |  |  | Article 30(3) |  | 2013-01-08
Gas | Combustion plants other than gas turbines and gas engines | 50 |  | 50 | 100 | 0.10204 | 0.17007 | Article 30(3) |  | 2013-01-08
Gas | Gas turbines (including CCGT) | 50 |  | 50 | 50 | 0.05102 | 0.085034 | Article 30(3) |  | 2013-01-08
Gas | Gas engines | 50 |  | 50 | 75 | 0.076531 | 0.12755 | Article 30(3) |  | 2013-01-08

## Data
Data from available Environmental Sustainabilty and Governance reports
Cells highlighted in this colour are the values taken from the ESG reports
Site Name | Fuel | Year | Total Generation Capacity (GW) | Annual Generation (TWh) | Lower bound | Upper bound | Annual NOx Emissions (tonnes) | Lower bound | Upper bound | Nox (g/kWh) | Max Nox | Min Nox | Positive Difference | Neg Diff | Source | Notes
Drax | Biomass | 2022 | 2.6 | 12.6415 | 12.5925 | 12.6905 | 5956 | 5955.5 | 5956.5 | 0.47115 | 0.47302 | 0.46929 | 0.001873 | 0.0018585 | https://www.drax.com/wp-content/uploads/2023/03/Drax_ESG2022_Single_Pages.pdf | Assumption made that proportion of Biomass to Hydro power same in 2021 and 2022
Drax | Coal | 2022 | 1.4 | 0.02 | 0.015 | 0.025 | 22 | 21.5 | 22.5 | 1.1 | 1.5 | 0.86 | 0.4 | 0.24 | https://www.drax.com/wp-content/uploads/2023/03/Drax_ESG2022_Single_Pages.pdf
Drax | Biomass | 2021 | 2.6 | 14.6994 | 14.6504 | 14.7484 | 6882 | 6881.5 | 6882.5 | 0.46818 | 0.46978 | 0.46659 | 0.0016 | 0.0015893 | https://www.drax.com/wp-content/uploads/2023/03/Drax_ESG2022_Single_Pages.pdf
Drax | Coal | 2021 | 1.4 | 1.1 | 1.05 | 1.15 | 534 | 533.5 | 534.5 | 0.48545 | 0.50905 | 0.46391 | 0.023593 | 0.021542 | https://www.drax.com/wp-content/uploads/2023/03/Drax_ESG2022_Single_Pages.pdf
Uniper Europe | Gas and Coal | 2022 | 14.8 | 36.3 | 36.25 | 36.35 | 11900 | 11850 | 11950 | 0.32782 | 0.32966 | 0.326 | 0.0018315 | 0.0018264 | https://www.uniper.energy/system/files/2023-04/2023-04-06_FY_2022_Uniper_Sustainability_Report_.pdf | This is all of the Uniper Coal and Gas Power plants combined
RWE Total | Lignite | 2022 | 7.6 | 12.2 | [5 empty] | 0.73 |  |  |  |  | https://www.rwe.com/-/media/RWE/documents/09-verantwortung-nachhaltigkeit/cr-berichte/sustainability-performance-report-2022.pdf | All of RWE
RWE Total | Hard Coal | 2022 | 1.5 | 1.3 | [5 empty] | 0.35 |  |  |  |  | https://www.rwe.com/-/media/RWE/documents/09-verantwortung-nachhaltigkeit/cr-berichte/sustainability-performance-report-2022.pdf | All of RWE
RWE Total | Gas | 2022 | 14.3 | 12.2 | [5 empty] | 0.14 |  |  |  |  | https://www.rwe.com/-/media/RWE/documents/09-verantwortung-nachhaltigkeit/cr-berichte/sustainability-performance-report-2022.pdf | All of RWE
RWE Total | Lignite | 2021 | 8.5 | 12 | [5 empty] | 0.78 |  |  |  |  | https://www.rwe.com/-/media/RWE/documents/09-verantwortung-nachhaltigkeit/cr-berichte/sustainability-performance-report-2022.pdf | All of RWE
RWE Total | Hard Coal | 2021 | 1.5 | 1.8 | [5 empty] | 0.37 |  |  |  |  | https://www.rwe.com/-/media/RWE/documents/09-verantwortung-nachhaltigkeit/cr-berichte/sustainability-performance-report-2022.pdf | All of RWE
RWE Total | Gas | 2021 | 14.3 | 14.9 | [5 empty] | 0.15 |  |  |  |  | https://www.rwe.com/-/media/RWE/documents/09-verantwortung-nachhaltigkeit/cr-berichte/sustainability-performance-report-2022.pdf | All of RWE

## DUKES 5.11 - May 2023
Table 5.11 List of major power producer power stations in the United Kingdom operational at the end of May 2023
This worksheet contains one table
Some cells refer to notes which can be found on the notes worksheet
Freeze panes are active on this sheet, to turn off freeze panes select the 'view' then 'freeze panes' then 'unfreeze panes' or use [Alt W, F]
Source - DUKES 5.11 - https://www.gov.uk/government/statistics/electricity-chapter-5-digest-of-united-kingdom-energy-statistics-dukes
This table contains empty cells, empty cells indicate data not applicable
Company Name | Site Name | Technology | Type | CHP | Primary Fuel | Secondary Fuel | InstalledCapacity (MW) | Grid Connection Type | Country | Region | Postcode | OS Reference | X-Coordinate | Y-Coordinate | Year Commissioned
Anesco | Abbey Fields | Solar | PV | No | Solar |  | 4.9421 | LV | England | South East | ME108HD |  |  |  | 2016
Anesco | Abergelli | Solar | PV | No | Solar |  | 7.6822 | LV | Wales | Wales | SA57NN |  | 265507.0 | 202009.0 | 2015
Anesco | Albrighton | Solar | PV | No | Solar |  | 4.9735 | LV | England | West Midlands | WV91RQ |  | 383987.0 | 305139.0 | 2017
Anesco | Anglesey | Solar | PV | No | Solar |  | 14.9261 | LV | Wales | Wales | LL635SZ |  | 238717.0 | 367342.0 | 2014
Anesco | Ashton | Solar | PV | No | Solar |  | 4.8082 | LV | England | South West | BA146DX |  | 388976.0 | 158134.0 | 2017
Anesco | Askern | Solar | PV | No | Solar |  | 4.9737 | LV | England | Yorkshire and Humber | DN60BZ |  | 455441.0 | 413876.0 | 2015
Anesco | Bake Farm | Solar | PV | No | Solar |  | 4.9993 | LV | Scotland | Scotland |  | NO564429 | 233036.0 | 58842.0 | 2015
Anesco | Barr Farm | Solar | PV | No | Solar |  | 1.885 | LV | England | [5 empty] | 2015
Anesco | Barton Close | Solar | PV | No | Solar |  | 4.6103 | LV | England | South West |  | SY651810 | 247374.0 | 141403.0 | 2015
Anesco | Basin Bridge | Solar | PV | No | Solar |  | 4.9896 | LV | England | East Midlands | CV136JJ |  |  |  | 2016
Anesco | Bedford | Solar | PV | No | Solar |  | 0.62934 | LV | England | East Midlands | MK443SD |  |  |  | 2016
Anesco | Berry Court | Solar | PV | No | Solar |  | 3.9203 | LV | England | South East | RG265AT |  | 461938.0 | 159221.0 | 2016
Anesco | Biglis | Solar | PV | No | Solar |  | 4.973 | LV | England | Wales | CF631BL |  |  |  | 2016
Anesco | Bilsthorpe | Solar | PV | No | Solar |  | 5.7408 | LV | England | East Midlands | NG228ST |  | 465147.0 | 361625.0 | 2014
Anesco | Blackdown | Solar | PV | No | Solar |  | 7.454 | LV | England | South West | TA37DY |  | 320819.0 | 114679.0 | 2014
Anesco | Blackwell Grange | Solar | PV | No | Solar |  | 4.9766 | LV | England | West Midlands | CV364PF |  | 422892.0 | 243330.0 | 2017
Anesco | Blisworth | Solar | PV | No | Solar |  | 3.588 | LV | England | East Midlands | NN73DA |  | 473113.0 | 252638.0 | 2016
Anesco | Blue House | Solar | PV | No | Solar |  | 4.9795 | LV | England | North East | TS225PW |  | 446965.0 | 526727.0 | 2016
Anesco | Bourne Park | Solar | PV | No | Solar |  | 0.2484 | LV | England | South West | DT27TU |  | 372107.0 | 97577.0 | 2012
Anesco | Bourne Park South | Solar | PV | No | Solar |  | 2.3997 | LV | England | South West | DT27TU |  | 372234.0 | 97408.0 | 2015
Anesco | Bridgwater | Solar | PV | No | Solar |  | 1.871 | LV | England | South West | TA70HY |  |  |  | 2016
Anesco | Bristol Water | Solar | PV | No | Solar |  | 0.80255 | LV | England | South West | GL139HN |  | 353895.0 | 167517.0 | 2017
Anesco | Brook Hall | Solar | PV | No | Solar |  | 4.6738 | LV | England | South West | BA149PT |  | 385169.0 | 153475.0 | 2016
Anesco | Brookbarn | Solar | PV | No | Solar |  | 3.63 | LV | England | South East | BN177PE |  | 500000.0 | 102000.0 | 2015
Anesco | Brookside | Solar | PV | No | Solar |  | 4.9974 | LV | England | West Midlands | CV379RG |  | 414476.0 | 254127.0 | 2016
Anesco | Broxted | Solar | PV | No | Solar |  | 31.59 | LV | England | Eastern |  | TQ637458 | 572387.0 | 251110.0 | 2013
Anesco | Bulls Head North | Solar | PV | No | Solar |  | 5.513 | LV | England | East Midlands | MK168LP |  | 481460.0 | 251327.0 | 2014
Anesco | Bumpers Farm | Solar | PV | No | Solar |  | 4.9971 | LV | England | South East | HP279RE |  | 476303.0 | 205882.0 | 2017
Anesco | Bumpers Farm 2 | Solar | PV | No | Solar |  | 12.0077 | LV | England | South East | HP279RE |  |  |  | 2020
Anesco | Chalgrove | Solar | PV | No | Solar |  | 2.402 | LV | England | [5 empty] | 2014
Anesco | Chard | Solar | PV | No | Solar |  | 3.043 | LV | England | South West | TA201RR |  |  |  | 2016
Anesco | Clayhill | Solar | PV | No | Solar |  | 9.8406 | LV | England | Eastern | MK455JD |  | 504351.0 | 233195.0 | 2017
Anesco | Coleford | Solar | PV | No | Solar |  | 3.4027 | LV | England | South West | GL168QD |  |  |  | 2016
Anesco | Cotgrave | Solar | PV | No | Solar |  | 4.9833 | LV | England | East Midlands | NG123GU |  | 463974.0 | 336042.0 | 2015
Anesco | Crow Trees | Solar | PV | No | Solar |  | 4.6931 | LV | England | East Midlands | NG171JF |  |  |  | 2016
Anesco | Culworth | Solar | PV | No | Solar |  | 3.6364 | LV | England | East Midlands | OX172HW |  | 454564.0 | 245985.0 | 2015
Anesco | Dale Farm | Solar | PV | No | Solar |  | 4.996 | LV | England | [5 empty] | 2018
Anesco | Darran | Solar | PV | No | Solar |  | 1.823 | LV | Wales | Wales |  |  |  |  | 2017
Anesco | Derwyn | Solar | PV | No | Solar |  | 4.664 | LV | England | Wales | CF623AA |  |  |  | 2016
Anesco | Dragon LNG | Solar | PV | No | Solar |  | 9.9727 | HV | Wales | Wales | SA73 1DR |  |  |  | 2022
Anesco | East Appleton | Solar | PV | No | Solar |  | 4.9795 | LV | England | Yorkshire and Humber | DL107QE |  | 423660.0 | 495768.0 | 2016
Anesco | East Farm | Solar | PV | No | Solar |  | 6.843 | LV | England | South West | BA120PG |  | 398727.0 | 142115.0 | 2013
Anesco | Eaton Hill | Solar | PV | No | Solar |  | 0.4743 | LV | England | West Midlands | HR60DG |  |  |  | 2015
Anesco | Eynsham | Solar | PV | No | Solar |  | 13.452 | LV | England | South East | OX296XD |  | 439658.0 | 210754.0 | 2014
Anesco | Fell View | Solar | PV | No | Solar |  | 4.2588 | LV | England | North West | PR25SD |  | 358322.0 | 433776.0 | 2016
Anesco | Gedling | Solar | PV | No | Solar |  | 5.7408 | LV | England | East Midlands | NG44JX |  | 461655.0 | 344045.0 | 2015
Anesco | Grantham | Solar | PV | No | Solar |  | 4.8787 | LV | England | East Midlands |  | SU508503 | 507000.0 | 392000.0 | 2015
Anesco | Granville | Solar | PV | No | Solar |  | 4.4372 | LV | England | West Midlands | TF28PQ |  | 372363.0 | 313370.0 | 2016
Anesco | Greencroft | Solar | PV | No | Solar |  | 4.9275 | LV | England | North East | DH97XR |  | 417307.0 | 550812.0 | 2016
Anesco | Grimsargh | Solar | PV | No | Solar |  | 2.9156 | LV | England | North West | PR25SD |  | 358322.0 | 433776.0 | 2016
Anesco | Guynd | Solar | PV | No | Solar |  | 4.9878 | LV | Scotland | Scotland |  | SK880386 | 356230.0 | 742772.0 | 2015
Anesco | Hadlow | Solar | PV | No | Solar |  | 18.9218 | LV | England | South East | CB89YD |  | 562879.0 | 145736.0 | 2015
Anesco | Hale | Solar | PV | No | Solar |  | 3.599 | LV | England | South West | BH236BB |  | 409997.0 | 97268.0 | 2015
Anesco | Hale Manor Farm | Solar | PV | No | Solar |  | 4.9993 | LV | England | South East | PO303AR |  |  |  | 2016
Anesco | Halse | Solar | PV | No | Solar |  | 8.3405 | LV | England | South West | TA43LY |  |  |  | 2013
Anesco | Hermitage | Solar | PV | No | Solar |  | 4.9988 | LV | England | Eastern | MK455JD |  | 503595.0 | 232813.0 | 2016
Anesco | Heywood Grange | Solar | PV | No | Solar |  | 4.9631 | LV | England | West Midlands | ST102PL |  | 396689.0 | 345502.0 | 2016
Anesco | High Meadow | Solar | PV | No | Solar |  | 3.8875 | LV | England | North East | TS211EA |  | 439442.0 | 521774.0 | 2016
Anesco | Higher Bye | Solar | PV | No | Solar |  | 6.7906 | LV | England | South West | TA230JT |  | 305042.0 | 142360.0 | 2015
Anesco | Homestead | Solar | PV | No | Solar |  | 3.9535 | LV | England | South East | PO410TZ |  | 439433.0 | 88404.0 | 2015
Anesco | Horam | Solar | PV | No | Solar |  | 2.571 | LV | England | South East | TN210JN |  | 556616.0 | 115760.0 | 2015
Anesco | Horsacott | Solar | PV | No | Solar |  | 6.54 | LV | England | South West | EX312PD |  |  |  | 2013
Anesco | Hungerford | Solar | PV | No | Solar |  | 4.4743 | LV | England | South East | RG278SW |  | 478178.0 | 153997.0 | 2016
Anesco | Huntingdon | Solar | PV | No | Solar |  | 10.204 | LV | England | Eastern | PE285YJ |  | 520021.0 | 281612.0 | 2014
Anesco | Hyde Farm | Solar | PV | No | Solar |  | 4.9421 | LV | England | South East | MK464DU |  | 488765.0 | 253909.0 | 2017
Anesco | Jordanston | Solar | PV | No | Solar |  | 4.631 | LV | Wales | Wales | SA708NQ |  |  |  | 2013
Anesco | Kent | Solar | PV | No | Solar |  | 4.857 | LV | England | South East | ME207FG |  |  |  | 2016
Anesco | Kinblethmont | Solar | PV | No | Solar |  | 4.9993 | LV | Scotland | Scotland |  | ST576232 | 363182.0 | 746857.0 | 2016
Anesco | Langley Priory | Solar | PV | No | Solar |  | 2.036 | LV | England | East Midlands | DE742QQ |  |  |  | 2015
Anesco | Lee Moor | Solar | PV | No | Solar |  | 4.9873 | LV | England | South West | PL75JP |  | 256033.0 | 60850.0 | 2016
Anesco | Lincoln Farm | Solar | PV | No | Solar |  | 10.6848 | LV | England | East Midlands | PE245AT |  |  |  | 2016
Anesco | Lindridge | Solar | PV | No | Solar |  | 4.9241 | LV | England | East Midlands | LE99FD |  |  |  | 2016
Anesco | Littlewood | Solar | PV | No | Solar |  | 5 | LV | England | North West | NG198JA |  |  |  | 2017
Anesco | Lodge Farm | Solar | PV | No | Solar |  | 4.8797 | LV | England | East Midlands | S445TE |  | 441566.0 | 370954.0 | 2015
Anesco | Low Burntoft | Solar | PV | No | Solar |  | 4.9982 | LV | England | North East | TS225PD |  | 445706.0 | 527911.0 | 2016
Anesco | Lucern | Solar | PV | No | Solar |  | 4.74 | LV | England | West Midlands | CV379RG |  | 415458.0 | 255809.0 | 2016
Anesco | Malmesbury | Solar | PV | No | Solar |  | 5 | LV | England | South West | SN169SR |  |  |  | 2016
Anesco | Mendip | Solar | PV | No | Solar |  | 7.175 | LV | England | South West | BA53AA |  | 359176.0 | 151234.0 | 2014
Anesco | Michaelston | Solar | PV | No | Solar |  | 4.1743 | LV | Wales | Wales | CF36XS |  | 322998.0 | 183674.0 | 2016
Anesco | Milborne Port | Solar | PV | No | Solar |  | 3.292 | LV | England | South West | DT95EF |  |  |  | 2017
Anesco | Milkwall | Solar | PV | No | Solar |  | 3.5006 | LV | England | South West | GL168QD |  |  |  | 2016
Anesco | Misson Park | Solar | PV | No | Solar |  | 4.9896 | LV | England | East Midlands | DN106DP |  |  |  | 2016
Anesco | Moneystone | Solar | PV | No | Solar |  | 4.9832 | LV | England | West Midlands | ST102DZ |  | 404572.0 | 346224.0 | 2016
Anesco | Moss Thorn | Solar | PV | No | Solar |  | 4.9735 | LV | England | North West | CA110BY |  | 348608.0 | 530601.0 | 2017
Anesco | Nancrossa | Solar | PV | No | Solar |  | 6.856 | LV | England | South West | TR109EA |  |  |  | 2016
Anesco | Nanthenfoel | Solar | PV | No | Solar |  | 4.9968 | LV | Wales | Wales | SA487NP |  | 254014.0 | 252465.0 | 2017
Anesco | Nether Mill | Solar | PV | No | Solar |  | 3.765 | LV | England | South West |  |  |  |  | 2015
Anesco | Newlands | Solar | PV | No | Solar |  | 4.9993 | LV | England | South West |  | SU115278 | 365099.0 | 81019.0 | 2015
Anesco | Newnton Dairy | Solar | PV | No | Solar |  | 7.176 | LV | England | South West | SN169SR |  | 392277.0 | 191968.0 | 2014
Anesco | Oak Cottage | Solar | PV | No | Solar |  | 4.8672 | LV | Wales | Wales | SA624PR |  | 202839.0 | 217801.0 | 2015
Anesco | Oakham | Solar | PV | No | Solar |  | 4.6396 | LV | England | South West | BS324BS |  | 359684.0 | 183393.0 | 2016
Anesco | Ollerton | Solar | PV | No | Solar |  | 4.2526 | LV | England | East Midlands | NG229DX |  | 463220.0 | 366009.0 | 2017
Anesco | Overton | Solar | PV | No | Solar |  | 3.7523 | LV | England | South East |  | TF459067 | 450500.0 | 150500.0 | 2015
Anesco | Owls Lodge | Solar | PV | No | Solar |  | 10.0046 | LV | England | South East | SP116PL |  | 443869.0 | 142971.0 | 2013
Anesco | Oxcroft | Solar | PV | No | Solar |  | 4.1897 | LV | England | East Midlands | S446AG |  | 446492.0 | 374323.0 | 2016
Anesco | Palmersford | Solar | PV | No | Solar |  | 3.036 | LV | England | South West | BH236BG |  | 409981.0 | 99040.0 | 2016
Anesco | Parcstormy | Solar | PV | No | Solar |  | 0.7 | LV | England | Wales | CF334RS |  |  |  | 2013
Anesco | Pen-Y-Cae | Solar | PV | No | Solar |  | 6.7623 | LV | Wales | Wales | SA183BJ |  | 260143.0 | 211806.0 | 2015
Anesco | Pierces Farm | Solar | PV | No | Solar |  | 1.7431 | LV | England | South East | RG71LY |  | 468119.0 | 167296.0 | 2015
Anesco | Playters | Solar | PV | No | Solar |  | 8.6295 | LV | England | Eastern | NR347TN |  | 644257.0 | 287733.0 | 2015
Anesco | Poplars | Solar | PV | No | Solar |  | 4.98 | LV | England | Eastern | CV379RG |  | 551077.0 | 298243.0 | 2016
Anesco | Portworthy | Solar | PV | No | Solar |  | 4.0239 | LV | England | South West | PL75JP |  | 256878.0 | 60850.0 | 2015
Anesco | Priors Byne | Solar | PV | No | Solar |  | 8.023 | LV | England | South East | RH138NX |  |  |  | 2015
Anesco | Puriton | Solar | PV | No | Solar |  | 4.5677 | LV | England | South West | TA64TG |  | 332462.0 | 142273.0 | 2011
Anesco | Puriton F | Solar | PV | No | Solar |  | 3.96 | LV | England | South West | TA78AD |  |  |  | 2016
Anesco | Radcliffe | Solar | PV | No | Solar |  | 4.1574 | LV | England | East Midlands | NG122LT |  | 463038.0 | 338202.0 | 2015
Anesco | Radford | Solar | PV | No | Solar |  | 4.9735 | LV | England | West Midlands | CV311XJ |  | 435175.0 | 261988.0 | 2015
Anesco | Rainbow | Solar | PV | No | Solar |  | 4.7907 | LV | England | South West | TA64TG |  | 331238.0 | 141809.0 | 2015
Anesco | Rymes | Solar | PV | No | Solar |  | 4.9991 | LV | England | South West | GL181HE |  |  |  | 2017
Anesco | Salcey Farm | Solar | PV | No | Solar |  | 5.4616 | LV | England | South East | MK168LP |  | 485184.0 | 250544.0 | 2014
Anesco | Salford Lodge | Solar | PV | No | Solar |  | 4.9962 | LV | England | West Midlands | WR118SN |  |  |  | 2015
Anesco | Sandridge | Solar | PV | No | Solar |  | 49.62 | LV | England | [5 empty] | 2015
Anesco | Sandys Moor | Solar | PV | No | Solar |  | 2.9 | LV | England | South West | TA42LY |  | 308509.0 | 127381.0 | 2013
Anesco | Shalfleet | Solar | PV | No | Solar |  | 4.996 | LV | England | South East | PO410TZ |  | 440587.0 | 88605.0 | 2015
Anesco | Sheep Shed | Solar | PV | No | Solar |  | 4.9858 | LV | England | West Midlands | CV379RG |  | 415469.0 | 255805.0 | 2016
Anesco | Sheepbridge | Solar | PV | No | Solar |  | 5 | LV | England | South East | RG71PX |  |  |  | 2016
Anesco | Shelswell | Solar | PV | No | Solar |  | 5.0633 | LV | England | South East | OX278EH |  | 460822.0 | 230982.0 | 2013
Anesco | Skylark | Solar | PV | No | Solar |  | 4.9389 | LV | England | Eastern | CB232SZ |  | 531754.0 | 257635.0 | 2013
Anesco | Slepe Farm | Solar | PV | No | Solar |  | 0.4984 | LV | England | South West | BH166HS |  | 392991.0 | 93161.0 | 2011
Anesco | Soho Farm | Solar | PV | No | Solar |  | 1.74 | LV | England | [5 empty] | 2014
Anesco | Southfield | Solar | PV | No | Solar |  | 9.7614 | LV | England | South West | CT67DZ |  | 357089.0 | 124014.0 | 2016
Anesco | Spear Hill | Solar | PV | No | Solar |  | 4.951 | LV | England | South East | RH203BA |  |  |  | 2016
Anesco | Spring Lane | Solar | PV | No | Solar |  | 0.958 | LV | England | East Midlands | LE651WU |  | 436639.0 | 314607.0 | 2017
Anesco | Steventon | Solar | PV | No | Solar |  | 10.0392 | LV | England | South East | OX136AP |  | 444299.0 | 192928.0 | 2014
Anesco | Stripe | Solar | PV | No | Solar |  | 4.9795 | LV | England | Yorkshire and Humber | DL107PW |  | 419640.0 | 502487.0 | 2016
Anesco | Stud Farm | Solar | PV | No | Solar |  | 2.3681 | LV | England | East Midlands | NG228SX |  | 464448.0 | 361853.0 | 2016
Anesco | Sutor | Solar | PV | No | Solar |  | 4.992 | LV | England | South West | BA99RA |  |  |  | 2016
Anesco | Swanland | Solar | PV | No | Solar |  | 4.998 | LV | England | London | EN63NH |  |  |  | 2017
Anesco | Thame | Solar | PV | No | Solar |  | 4.7916 | LV | England | South East | OX93QH |  | 473366.0 | 206186.0 | 2016
Anesco | The Beeches | Solar | PV | No | Solar |  | 4.9998 | LV | England | West Midlands | CV379RG |  | 414445.0 | 254098.0 | 2016
Anesco | The Leys | Solar | PV | No | Solar |  | 4.9795 | LV | England | West Midlands | CV379RG |  | 415118.0 | 253833.0 | 2016
Anesco | The Oaks | Solar | PV | No | Solar |  | 4.736 | LV | England | West Midlands | CV379RG |  | 415458.0 | 255809.0 | 2016
Anesco | The Rushes | Solar | PV | No | Solar |  | 4.9795 | LV | England | West Midlands | CV379RG |  | 416507.0 | 255215.0 | 2016
Anesco | The Willows | Solar | PV | No | Solar |  | 4.734 | LV | England | West Midlands | CV379RG |  | 410262.0 | 333700.0 | 2016
Anesco | Tope Farm | Solar | PV | No | Solar |  | 3.312 | LV | England | South West | TQ97DR |  | 283048.0 | 52733.0 | 2014
Anesco | Trickey Warren | Solar | PV | No | Solar |  | 4.632 | LV | England | South West | TA37DY |  | 320109.0 | 114779.0 | 2015
Anesco | Troughton | Solar | PV | No | Solar |  | 30.866 | LV | England | South West | GL207BW |  |  |  | 2016
Anesco | Tump Farm | Solar | PV | No | Solar |  | 4.998 | LV | England | South West | NP167HN |  |  |  | 2017
Anesco | Wally Corner | Solar | PV | No | Solar |  | 4.997 | LV | England | [5 empty] | 2017
Anesco | Warren | Solar | PV | No | Solar |  | 4.9889 | LV | England | South East | SO519AG |  | 437906.0 | 121342.0 | 2016
Anesco | Watchfield | Solar | PV | No | Solar |  | 10.6998 | LV | England | South West | TA94LD |  | 334135.0 | 147772.0 | 2014
Anesco | Waycock | Solar | PV | No | Solar |  | 7.3568 | LV | Wales | Wales | CF623AA |  |  |  | 2016
Anesco | Welbeck | Solar | PV | No | Solar |  | 11.2608 | LV | England | East Midlands | NG209PU |  | 457669.0 | 369999.0 | 2014
Anesco | West Field | Solar | PV | No | Solar |  | 4.9398 | LV | England | North West | PR30PU |  |  |  | 2016
Anesco | Whilton | Solar | PV | No | Solar |  | 0.40392 | LV | England | East Midlands | NN112NH |  |  |  | 2016
Anesco | Whitchurch | Solar | PV | No | Solar |  | 6.52 | LV | England | South West | BA34DW |  | 363439.0 | 153553.0 | 2014
Anesco | Willows Farm | Solar | PV | No | Solar |  | 4.62 | LV | England | West Midlands | WR114TG |  |  |  | 2016
Anesco | Wisbech | Solar | PV | No | Solar |  | 3.4047 | LV | England | Eastern |  | NO633470 | 546000.0 | 307000.0 | 2015
Anesco | Woodtown | Solar | PV | No | Solar |  | 2.7194 | LV | England | South West | BH228SW |  | 409156.0 | 97807.0 | 2015
Anesco | Wreay | Solar | PV | No | Solar |  | 4.9754 | LV | England | North West | CA40PY |  | 342315.0 | 547311.0 | 2017
Anesco | Wymeswold | Solar | PV | No | Solar |  | 2.1278 | LV | England | East Midlands | LE126UA |  | 460007.0 | 323259.0 | 2016
Anesco | Wymeswold - Wide Lane | Solar | PV | No | Solar |  | 4.2796 | LV | England | East Midlands | LE126SE |  | 463380.0 | 323140.0 | 2016
Anesco | Yarburgh | Solar | PV | No | Solar |  | 8.0861 | LV | England | East Midlands | LN11ONU |  | 534300.0 | 391971.0 | 2015
Atmosclear | Barton | Solar | PV | No | Solar |  | 1.2 | LV | England | South West |  |  | 307778.0 | 117118.0 | 2012
Atmosclear | Broadgate | Solar | PV | No | Solar |  | 1.1 | LV | England | South West |  |  | 277641.0 | 107308.0 | 2012
Atmosclear | Copley Wood (Renewables (SW) | Solar | PV | No | Solar |  | 1.5 | LV | England | South West |  |  |  |  | 2015
Atmosclear | Higher Pirzwell | Solar | PV | No | Solar |  | 1.2 | LV | England | South West |  |  | 307546.0 | 109156.0 | 2012
Atmosclear | Kia-Ora Farm | Solar | PV | No | Solar |  | 1.8 | LV | England | South West |  |  | 300975.0 | 107058.0 | 2013
Atmosclear | Long Ash Lane Solar Park | Solar | PV | No | Solar |  | 5 | LV | England | South West |  |  | 360928.0 | 102540.0 | 2017
Atmosclear | Luson | Solar | PV | No | Solar |  | 1.9 | LV | England | South West |  |  | 262016.0 | 53112.0 | 2013
Atmosclear | Stables Farm | Solar | PV | No | Solar |  | 1 | LV | England | South East |  |  | 440920.0 | 88770.0 | 2012
Atmosclear | Yeowood | Solar | PV | No | Solar |  | 1.2 | LV | England | South West |  |  | 344385.0 | 162232.0 | 2012
Babcock International and Fluor Inc | Maentwrog | Hydro | Natural Flow | No | Hydro |  | 35.3 | HV | Wales | Wales | LL414HY |  | 267297.81261199998 | 337806.87196800002 | 1928
BayWa R.E | Bagmoor Wind Ltd | Wind | Onshore | No | Wind |  | 16 | HV | England | Yorkshire and Humber | DN159GH |  | 488240.0 | 415400.0 | 2009
BayWa R.E | Scout Moor Wind Farm Ltd | Wind | Onshore | No | Wind |  | 65 | HV | England | North West | OL127TY |  | 382400.0 | 419200.0 | 2008
BayWa R.E | Tir Mostyn & Foel Goch Ltd | Wind | Onshore | No | Wind |  | 21.25 | HV | Wales | Wales | LL165RN |  | 300300.0 | 358800.0 | 2005
Bluefield Services | Bradenstoke Solar Park Ltd | Solar | PV | No | Solar |  | 69.7884 | LV | England | South West | SN154PZ |  | 402315.0 | 178635.0 | 2015
Calon Energy | Severn Power Ltd | Fossil Fuel | CCGT | No | Natural Gas |  | 850 | HV | England | 0 |  |  | 333250.0 | 185006.0 | 2010
Calon Energy | SUTTON BRIDGE POWER GENERATION | Fossil Fuel | CCGT | No | Natural Gas |  | 819 | HV | England | 0 |  |  | 547836.0 | 321256.0 | 1999
Capital Dynamics UK | Airfield Poddington | Wind | Onshore | No | Wind |  | 8.55 | LV | Scotland | [5 empty] | 2017
Capital Dynamics UK | Crockandun | Wind | Onshore | No | Wind |  | 15 | LV | Scotland | [5 empty] | 2017
Capital Dynamics UK | Daintree | Wind | Onshore | No | Wind |  | 4 | LV | England | East Midlands | NN67GW |  | 457545.0 | 272243.0 | 2014
Capital Dynamics UK | Dunmore | Wind | Onshore | No | Wind |  | 21 | LV | Northern Ireland | Northern Ireland |  |  |  |  | 2014
Capital Dynamics UK | East Youlstone | Wind | Onshore | No | Wind |  | 4 | LV | England | South West | EX239PU |  | 227610.0 | 115654.0 | 2015
Capital Dynamics UK | Elginny | Wind | Onshore | No | Wind |  | 23 | LV | Northern Ireland | Northern Ireland |  |  |  |  | 2018
Capital Dynamics UK | Falkirk Tod Hill | Wind | Onshore | No | Wind |  | 11.4 | LV | Scotland | [5 empty] | 2015
Capital Dynamics UK | Garlenick | Wind | Onshore | No | Wind |  | 4 | LV | England | South West | TR24RQ |  | 194662.0 | 49203.0 | 2014
Capital Dynamics UK | Harthill Torrance | Wind | Onshore | No | Wind |  | 5.7 | LV | Scotland | Scotland |  |  |  |  | 2015
Capital Dynamics UK | Middle Balbeggie | Wind | Onshore | No | Wind |  | 6.4 | LV | Scotland | Scotland |  |  |  |  | 2016
Capital Dynamics UK | Mossmorran | Wind | Onshore | No | Wind |  | 4.6 | HV | Scotland | Scotland |  | NT1793489429 | 318109.0 | 689419.0 | 2016
Capital Dynamics UK | Potato Pot | Wind | Onshore | No | Wind |  | 7.05 | LV | Scotland | [5 empty] | 2016
Capital Dynamics UK | Red Gap | Wind | Onshore | No | Wind |  | 12.5 | LV | Scotland | [5 empty] | 2017
Capital Dynamics UK | Rymes | Solar | PV | No | Solar |  | 4.9908 | LV | Wales | [5 empty] | 2017
Capital Dynamics UK | Seegronan | Wind | Onshore | No | Wind |  | 13.8 | LV | Scotland | [5 empty] | 2016
Capital Dynamics UK | Shantavny | Wind | Onshore | No | Wind |  | 16.1 | LV | Scotland | [5 empty] | 2017
Capital Dynamics UK | Watford Lodge | Wind | Onshore | No | Wind |  | 10.25 | LV | Scotland | [5 empty] | 2015
Capital Dynamics UK | Westnewton (BEGL4) | Wind | Onshore | No | Wind |  | 6.15 | LV | Scotland | [5 empty] | 2014
Capital Dynamics UK | Whiteside Hill | Wind | Onshore | No | Wind |  | 28.5 | HV | Scotland | [5 empty] | 2018
Capital Dynamics UK | Wythegill | Wind | Onshore | No | Wind |  | 1.5 | HV | England | North West |  | NY0121131657 | 301881.0 | 532072.0 | 2015
Capital Dynamics UK | Ysgellog | Wind | Onshore | No | Wind |  | 4.6 | LV | Wales | Wales | LL060AW |  | 240490.0 | 391238.0 | 2013
Co-owned by SSE Group and Cheung Kong Infrastructure Ltd | Seabank Power Ltd | Fossil Fuel | CCGT | No | Natural Gas |  | 1234 | HV | England | South West |  |  | 343425.0 | 161749.0 | 2000
Co-owned by SSE Group and Wheelabrator Technologies Inc | FM1 | Bioenergy | Bioenergy | No | MSW |  | 79 | LV | England | Yorkshire and Humber |  |  | 447490.0 | 424684.0 | 2015
Co-owned by SSE Group and Wheelabrator Technologies Inc | FM2 | Bioenergy | Bioenergy | No | MSW |  | 79 | LV | England | Yorkshire and Humber |  |  | 447490.0 | 424684.0 | 2019
Cubico Sustainable Investments | Chiplow | Wind | Onshore | No | Wind |  | 8.2 | LV | England | Eastern | PE318SR |  |  |  | 2016
Cubico Sustainable Investments | Kelmarsh | Wind | Onshore | No | Wind |  | 12.3 | LV | England | East Midlands | NN69LZ |  |  |  | 2016
Cubico Sustainable Investments | Middlewick | Wind | Onshore | No | Wind |  | 20.7 | LV | England | Eastern | CM07JQ |  | 600140.0 | 200001.0 | 2014
Cubico Sustainable Investments | Owls Hatch | Solar | PV | No | Solar |  | 51.9376 | LV | England | South East |  |  | 615860.0 | 165945.0 | 2015
Cubico Sustainable Investments | Penmanshiel | Wind | Onshore | No | Wind |  | 28.7 | LV | Scotland | Scotland | TD113RP |  | 380006.0 | 667129.0 | 2016
Cubico Sustainable Investments | Wandylaw | Wind | Onshore | No | Wind |  | 20.5 | LV | England | North East | NE675HG |  |  |  | 2013
Cubico Sustainable Investments | Winwick | Wind | Onshore | No | Wind |  | 12.3 | LV | England | East Midlands | NN67NS |  |  |  | 2016
Drax Power | Ffestiniog | Pumped hydro | Pumped hydro | No | Pumped hydro |  | 360 | HV | Wales | Wales |  | SH679444 | 267900.0 | 344400.0 | 1963
E.ON | Blackburn Meadows | Bioenergy | Bioenergy | Yes | Biomass |  | 34 | LV | England | Yorkshire and Humber |  | SK3950991482 | 440075.0 | 391650.0 | 2015
E.ON | Steven's Croft | Bioenergy | Bioenergy | Yes | Biomass |  | 46 | LV | Scotland | Scotland |  |  | 312100.0 | 585100.0 | 2007
Ecotricity | Alveston | Wind | Onshore | No | Wind |  | 6.9 | LV | England | South West | BS353TD |  | 365450.0 | 186055.0 | 2017
Ecotricity | Ballymena | Wind | Onshore | No | Wind |  | 4.6 | LV | Northern Ireland | Northern Ireland | BT424HZ |  | 130743.0 | 561194.0 | 2013
Ecotricity | Bambers | Wind | Onshore | No | Wind |  | 9.6 | LV | England | East Midlands | LN112QW |  | 549500.0 | 383600.0 | 2004
Ecotricity | Bristol Port | Wind | Onshore | No | Wind |  | 6 | LV | England | South West | BS119DQ |  | 350907.0 | 179457.0 | 2007
Ecotricity | Cardiff | Wind | Onshore | No | Wind |  | 2.3 | LV | Wales | Wales | CF32EE |  | 323460.0 | 179215.0 | 2011
Ecotricity | Dagenham | Wind | Onshore | No | Wind |  | 5.9 | LV | England | London | RM96SA |  | 550300.0 | 181600.0 | 2004
Ecotricity | Dalby | Wind | Onshore | No | Wind |  | 7.29 | LV | England | East Midlands | LE143LY |  | 465397.0 | 322239.0 | 2016
Ecotricity | Dundee | Wind | Onshore | No | Wind |  | 4 | LV | Scotland | Scotland | DD88UQ |  | 269652.0 | 688422.0 | 2006
Ecotricity | East Kilbride | Wind | Onshore | No | Wind |  | 0.6 | LV | Scotland | Scotland | G750ZZ |  | 264500.0 | 652000.0 | 2001
Ecotricity | Ecotech | Wind | Onshore | No | Wind |  | 1.5 | LV | England | Eastern | PE377HT |  | 0.0 | 0.0 | 1999
Ecotricity | Fen Farm | Wind | Onshore | No | Wind |  | 16 | LV | England | East Midlands | LN117LU |  | 537585.0 | 393825.0 | 2007
Ecotricity | Fen Farm Solar | Solar | PV | No | Solar |  | 0.9 | LV | England | East Midlands | LN117BP |  | 537585.0 | 393825.0 | 2011
Ecotricity | Galsworthy | Wind | Onshore | No | Wind |  | 9.2 | LV | England | South West | EX395NP |  | 240007.0 | 115922.0 | 2014
Ecotricity | Green Park | Wind | Onshore | No | Wind |  | 2 | LV | England | South East | RG26UE |  | 470755.0 | 169271.0 | 2005
Ecotricity | H&H | Wind | Onshore | No | Wind |  | 0.81 | LV | England | Yorkshire and Humber | DN140BA |  | 0.0 | 0.0 | 2016
Ecotricity | Lynch Knoll | Wind | Onshore | No | Wind |  | 0.5 | LV | England | South West | GL103UJ |  | 381600.0 | 200400.0 | 1996
Ecotricity | Mablethorpe | Wind | Onshore | No | Wind |  | 1.2 | LV | England | East Midlands | LN122QW |  | 548900.0 | 382500.0 | 2002
Ecotricity | QEH | Wind | Onshore | No | Wind |  | 0.81 | LV | England | Eastern | PE304ET |  | 565228.0 | 320492.0 | 2016
Ecotricity | RSPB | Wind | Onshore | No | Wind |  | 0.81 | LV | England | Eastern | SG192DL |  | 0.0 | 0.0 | 2016
Ecotricity | Shooters | Wind | Onshore | No | Wind |  | 2 | LV | England | South West | BA34LU |  | 359380.0 | 150740.0 | 2008
Ecotricity | Somerton | Wind | Onshore | No | Wind |  | 1.8 | LV | England | Eastern | NR294EY |  | 646900.0 | 318800.0 | 2000
Ecotricity | Swaffham II | Wind | Onshore | No | Wind |  | 1.8 | LV | England | Eastern | PE377HL |  | 582197.0 | 309324.0 | 2003
Ecotricity | Worksop | Wind | Onshore | No | Wind |  | 2 | LV | England | East Midlands | S802PU |  | 461695.0 | 378487.0 | 2009
Ecotricity Limited | Bulkworthy Solar | Solar | PV | No | Solar |  | 6.235 | Distribution Network | England | South West | EX22 7UP | SS404147 |  |  | 2022
Ecotricity Limited | Dalby Solar | Solar | PV | No | Solar |  | 6.88 | Distribution Network | England | East Midlands | LE14 3LY | SK648232 |  |  | 2022
EDF Energy | Barmoor | Wind | Onshore | No | Wind |  | 12 | LV | England | North East | TD152QD |  | 393797.0 | 634046.0 | 2014
EDF Energy | Beckburn | Wind | Onshore | No | Wind |  | 31.05 | LV | England | North West | DG165HU |  | 334466.0 | 568940.0 | 2017
EDF Energy | Bicker Fen | Wind | Onshore | No | Wind |  | 26 | LV | England | East Midlands | PE203BF |  | 519870.0 | 339325.0 | 2008
EDF Energy | Blyth | Wind | Offshore | No | Wind |  | 40 | LV | England | North East | NE227FB |  | 438227.0 | 582010.0 | 2018
EDF Energy | Boundary Lane | Wind | Onshore | No | Wind |  | 6.15 | LV | England | North East | DH89LQ |  | 404708.0 | 550336.0 | 2013
EDF Energy | Broomhill | Wind | Onshore | No | Wind |  | 8 | LV | England | North East | DL134LY |  | 415500.0 | 539500.0 | 2009
EDF Energy | Burnfoot | Wind | Onshore | No | Wind |  | 30.1 | LV | Scotland | Scotland | FK147JZ |  | 290135.0 | 703250.0 | 2010
EDF Energy | Burnfoot East | Wind | Onshore | No | Wind |  | 10.8 | LV | Scotland | Scotland | FK147JZ |  |  |  | 2020
EDF Energy | Burnhead Moss | Wind | Onshore | No | Wind |  | 26 | LV | Scotland | Scotland | FK12JW |  | 288503.0 | 671903.0 | 2016
EDF Energy | Cemmaes | Wind | Onshore | No | Wind |  | 15.3 | LV | Wales | Wales | SY209PR |  | 286800.0 | 306000.0 | 2002
EDF Energy | Corriemoillie | Wind | Onshore | No | Wind |  | 48.45 | HV | Scotland | Scotland | IV232PQ |  | 234700.0 | 867700.0 | 2017
EDF Energy | Deeping | Wind | Onshore | No | Wind |  | 16 | LV | England | East Midlands | PE113DD |  | 519905.0 | 316471.0 | 2006
EDF Energy | Dorenell | Wind | Onshore | No | Wind |  | 177 | HV | Scotland | Scotland | AB554DT |  | 332000.0 | 829500.0 | 2018
EDF Energy | Fairfield | Wind | Onshore | No | Wind |  | 6.5 | LV | England | North West | CA144QE |  | 301826.0 | 521459.0 | 2011
EDF Energy | Fallago Rig | Wind | Onshore | No | Wind |  | 144 | HV | Scotland | Scotland | TD36NW |  | 357000.0 | 660000.0 | 2013
EDF Energy | Glassmoor I | Wind | Onshore | No | Wind |  | 16 | LV | England | Eastern | PE262TS |  | 543128.0 | 292192.0 | 2006
EDF Energy | Glassmoor II | Wind | Onshore | No | Wind |  | 12.3 | LV | England | Eastern | PE262TS |  | 528421.0 | 292867.0 | 2013
EDF Energy | Great Orton | Wind | Onshore | No | Wind |  | 3.96 | LV | England | North west | CA70JY |  | 331300.0 | 553400.0 | 1999
EDF Energy | Green Rigg | Wind | Onshore | No | Wind |  | 36 | LV | England | North East | NE482EY |  | 392000.0 | 582000.0 | 2012
EDF Energy | Hartlepool | Nuclear | AGR | No | Nuclear |  | 1185 | HV | England | North East | TS252BZ |  | 451747.0 | 531078.0 | 1983
EDF Energy | Heysham 1 | Nuclear | AGR | No | Nuclear |  | 1060 | HV | England | North West | LA32XH |  | 341498.0 | 461449.0 | 1983
EDF Energy | Heysham 2 | Nuclear | AGR | No | Nuclear |  | 1240 | HV | England | North West | LA32XH |  | 341498.0 | 461449.0 | 1988
EDF Energy | High Hedley I | Wind | Onshore | No | Wind |  | 2.4 | LV | England | North East | DL134PR |  | 415700.0 | 541000.0 | 2001
EDF Energy | High Hedley II | Wind | Onshore | No | Wind |  | 5.2 | LV | England | North East | DL134PR |  | 415700.0 | 541000.0 | 2008
EDF Energy | Kirkheaton | Wind | Onshore | No | Wind |  | 1.8 | LV | England | North East | NE192DQ |  | 400800.0 | 576900.0 | 2000
EDF Energy | Langley | Wind | Onshore | No | Wind |  | 8 | LV | England | North East | DH70EE |  | 420928.0 | 547703.0 | 2008
EDF Energy | Llangwyryfon | Wind | Onshore | No | Wind |  | 9.35 | LV | Wales | Wales | SY234SR |  | 261752.0 | 269577.0 | 2003
EDF Energy | Longpark | Wind | Onshore | No | Wind |  | 38 | LV | Scotland | Scotland | TD12SW |  | 348050.0 | 642050.0 | 2009
EDF Energy | Park Spring | Wind | Onshore | No | Wind |  | 8.55 | LV | England | Yorkshire and Humber | EH558RT |  | 439689.0 | 408763.0 | 2015
EDF Energy | Pearie Law | Wind | Onshore | No | Wind |  | 19.2 | LV | Scotland | Scotland | EH558RT |  | 302205.0 | 659690.0 | 2016
EDF Energy | Red House | Wind | Onshore | No | Wind |  | 12 | LV | England | East Midlands | PE129NG |  | 542000.0 | 329000.0 | 2006
EDF Energy | Red Tile | Wind | Onshore | No | Wind |  | 24 | LV | England | South East | PE282JX |  | 523939.0 | 271933.0 | 2007
EDF Energy | Rhodders | Wind | Onshore | No | Wind |  | 12.3 | LV | Scotland | Scotland | FK147JZ |  | 288738.0 | 697461.0 | 2016
EDF Energy | Roade | Wind | Onshore | No | Wind |  | 7.2 | LV | England | East Midlands | NN72EG |  | 477964.0 | 252105.0 | 2014
EDF Energy | Rusholme | Wind | Onshore | No | Wind |  | 24 | LV | England | Yorkshire and Humber | YO88PX |  | 469500.0 | 426500.0 | 2010
EDF Energy | Sizewell B | Nuclear | PWR | No | Nuclear |  | 1198 | HV | England | Eastern | IP164UR |  | 647453.0 | 260420.0 | 1995
EDF Energy | Teesside | Wind | Offshore | No | Wind |  | 62 | LV | England | North East | TS240RQ |  | 458470.0 | 528174.0 | 2013
EDF Energy | Torness | Nuclear | AGR | No | Nuclear |  | 1200 | HV | Scotland | Scotland | EH421QS |  | 218252.0 | 651517.0 | 1988
EDF Energy | Trimdon | Wind | Onshore | No | Wind |  | 5.2 | LV | England | North East | TS296NR |  | 436000.0 | 536300.0 | 2008
EDF Energy | Walkway | Wind | Onshore | No | Wind |  | 14 | LV | England | North East | TS225NS |  | 439000.0 | 530000.0 | 2008
Eneco Wind UK | Burn of Whilk | Wind | Onshore | No | Wind |  | 22.5 | LV | Scotland | Scotland |  | ND293407 | 326232.0 | 939965.0 | 2015
Eneco Wind UK | Lochluichart | Wind | Onshore | No | Wind |  | 69 | HV | Scotland | Scotland |  | NH333680 | 232030.0 | 866235.0 | 2013
Eneco Wind UK | Moy | Wind | Onshore | No | Wind |  | 66 | LV | Scotland | Scotland |  | NH779370 | 276741.0 | 835240.0 | 2016
Eneco Wind UK | Oaklands | Solar | PV | No | Solar |  | 5 | LV | England | South West |  | SY900894 | 389957.0 | 89555.0 | 2015
Eneco Wind UK | Tullo | Wind | Onshore | No | Wind |  | 17.5 | LV | Scotland | Scotland |  | NO757723 | 387283.0 | 785873.0 | 2010
Eneco Wind UK | Twinshiels | Wind | Onshore | No | Wind |  | 25 | LV | Scotland | Scotland |  | NO757723 | 375955.0 | 771728.0 | 2014
Energy Capital Partners | Indian Queens Power Ltd | Fossil Fuel | Single cycle | No | Diesel/Gas Oil |  | 140 | HV | England | South West |  | SW940591 | 191739.0 | 58385.0 | 1996
Energy Capital Partners | Saltend Power Station | Fossil Fuel | CCGT | Yes | Natural Gas |  | 1200 | HV | England | Yorkshire and Humber | HU128GA |  | 509793.0 | 428825.0 | 2000
Engie Power | Barlockhart Moor Wind Energy Ltd | Wind | Onshore | No | Wind |  | 8.2 | HV | Scotland | Scotland | DG80JQ |  | 221183.0 | 555886.0 | 2013
Engie Power | Blantyre Muir Wind Energy Ltd | Wind | Onshore | No | Wind |  | 12.3 | HV | Scotland | Scotland | G720TR |  | 268888.0 | 651781.0 | 2014
Engie Power | Cairnborrow Wind Energy Ltd | Wind | Onshore | No | Wind |  | 10.25 | HV | Scotland | Scotland | AB544XP |  | 346153.0 | 841867.0 | 2017
Engie Power | Capel Grange Solar Energy Ltd | Solar | PV | No | Solar |  | 4.08 | LV | England | South East | TN126QX |  | 565242.0 | 144832.0 | 2016
Engie Power | Carsington Wind Energy Ltd | Wind | Onshore | No | Wind |  | 8.2 | HV | England | East Midlands | DE44HF |  | 424640.0 | 354200.0 | 2014
Engie Power | Crimp Wind Power Ltd | Wind | Onshore | No | Wind |  | 2.43 | HV | England | South West | EX239PD |  | 225180.0 | 115445.0 | 2011
Engie Power | Flimby Wind Energy Ltd | Wind | Onshore | No | Wind |  | 6.15 | HV | England | North West | CA158SU |  | 302500.0 | 533500.0 | 2013
Engie Power | Scotia Wind (Craigengelt) Ltd | Wind | Onshore | No | Wind |  | 20 | HV | Scotland | Scotland | FK79QS |  | 272451.0 | 686495.0 | 2010
Engie Power | Sober Hill Wind Farm Ltd | Wind | Onshore | No | Wind |  | 12.3 | HV | England | Yorkshire and Humber | YO434TG |  | 480972.0 | 437663.0 | 2013
EPR | EPR Ely Ltd | Bioenergy | Bioenergy | No | Biomass | Natural Gas | 40 | HV | England | Eastern | CB62QE |  | 545000.0 | 279900.0 | 2001
EPR | EPR Eye Ltd | Bioenergy | Bioenergy | No | Biomass | Oil | 14.316 | HV | England | Eastern | IP238BW |  | 613050.0 | 275050.0 | 1992
EPR | EPR Glanford Ltd | Bioenergy | Bioenergy | No | Biomass | Oil | 14 | HV | England | Eastern | DN158SB |  | 486050.0 | 415050.0 | 1993
EPR | EPR Scotland Ltd | Bioenergy | Bioenergy | No | Biomass | Oil | 12.5 | HV | Scotland | Scotland | KY50HR |  | 319000.0 | 695100.0 | 2000
EPR | EPR Thetford Ltd | Bioenergy | Bioenergy | No | Biomass | Oil | 41.5 | HV | England | Eastern | IP241LX |  | 585300.0 | 286900.0 | 1998
EPR | Ovenden Moor | Wind | Onshore | No | Wind |  | 18 | LV | England | Yorkshire and Humber |  |  | 404300.0 | 430900.0 | 1993
EPR | Royd Moor | Wind | Onshore | No | Wind |  | 6.5 | LV | England | Yorkshire and Humber |  |  | 422000.0 | 404000.0 | 1993
EPUKi | EP Ballylumford | Fossil Fuel | Single cycle | No | Diesel/Gas Oil |  | 116 | HV | Northern Ireland | Northern Ireland | BT403RS |  | 156969.0 | 556595.0 | 1974
EPUKi | EP Ballylumford CCGT | Fossil Fuel | CCGT | No | Natural Gas |  | 616 | HV | Northern Ireland | Northern Ireland | BT403RS |  | 156969.0 | 556595.0 | 2003
EPUKi | EP Kilroot | Fossil Fuel | Single cycle | No | Diesel/Gas Oil |  | 143.2 | HV | Northern Ireland | Northern Ireland | BT387LX |  | 157669.0 | 543287.0 | 1981
EPUKi | EP Kilroot Main Thermal | Fossil Fuel | Conventional steam | No | Coal | Oil | 559 | HV | Northern Ireland | Northern Ireland | BT387LX |  | 157669.0 | 543287.0 | 1981
EPUKi | EP Langage Ltd | Fossil Fuel | CCGT | No | Natural Gas |  | 905 | HV | England | South West | PL75AW |  | 257085.0 | 56194.0 | 2010
EPUKi | EP SHB Ltd | Fossil Fuel | CCGT | No | Natural Gas |  | 1365 | HV | England | Yorkshire and Humber | DN418BZ |  | 520457.0 | 409164.0 | 1997
EPUKi | Lynemouth Power Ltd | Bioenergy | Bioenergy | No | Biomass |  | 420 | HV | England | North East | NE639NW |  | 429850.0 | 590374.0 | 2018
ESB | Carrington Power | Fossil Fuel | CCGT | No | Natural Gas |  | 910 | HV | England | North West | M314AY |  | 373287.0 | 393037.0 | 2016
ESB | CoolkeeraghESB C30 | Fossil Fuel | CCGT | No | Natural Gas |  | 413 | HV | Northern Ireland | Northern Ireland | BT476UL |  | 64846.0 | 584768.0 | 2004
ESB | CoolkeeraghESB GT8 | Fossil Fuel | Single cycle | No | Diesel/Gas Oil |  | 53 | HV | Northern Ireland | Northern Ireland | BT476UL |  | 64846.0 | 584768.0 | 1970
ESB | Corby Power Station | Fossil Fuel | CCGT | No | Natural Gas |  | 407 | HV | England | East Midlands |  |  | 488447.0 | 266932.0 | 1994
European Energy A/S | Canewdon CIC | Solar | PV | No | Solar |  | 4.99 | LV | England | South East | SS43LW |  |  |  | 2022
European Energy A/S | Canewdon PV | Solar | PV | No | Solar |  | 4.99 | LV | England | South East | SS43LW |  |  |  | 2022
European Energy A/S | High Leas PV | Solar | PV | No | Solar |  | 4.88 | LV | England | East Midlands | LN118PJ |  |  |  | 2022
European Energy A/S | Parc Cynog | Wind | Onshore | No | Wind |  | 3.6 | LV | Wales | Wales |  |  | 225500.0 | 209500.0 | 2001
European Energy A/S | Pendine Wind Farm Limited | Wind | Onshore | No | Wind |  | 4.8 | LV | Wales | Wales |  |  | 225230.0 | 209760.0 | 2009
European Energy A/S | PV@Pendine Solar Farm | Solar | PV | No | Solar |  | 4.9 | LV | Wales | Wales |  |  | 224103.0 | 210103.0 | 2016
European Energy A/S | West End Farm PV | Solar | PV | No | Solar |  | 4.88 | LV | England | East Midlands | DN220EF |  |  |  | 2022
European Energy A/S | West End Farm PV CIC | Solar | PV | No | Solar |  | 4.88 | LV | England | East Midlands | DN220EF |  |  |  | 2022
European Energy A/S | Woodhouse PV | Solar | PV | No | Solar |  | 4.88 | LV | England | North East | SR53NS |  |  |  | 2022
Falck Renewables SpA | Assel Valley | Wind | Onshore | No | Wind |  | 25 | LV | Scotland | Scotland |  | NX211938 | 223370.0 | 595995.0 | 2016
Falck Renewables SpA | Auchrobert | Wind | Onshore | No | Wind |  | 38.76 | LV | Scotland | Scotland |  | NS760392 | 275154.0 | 638500.0 | 2017
Falck Renewables SpA | Ben Aketil | Wind | Onshore | No | Wind |  | 27.6 | LV | Scotland | Scotland |  | NG311485 | 132500.0 | 846500.0 | 2007
Falck Renewables SpA | Boyndie | Wind | Onshore | No | Wind |  | 16.3 | LV | Scotland | Scotland |  | NJ613641 | 364000.0 | 862000.0 | 2006
Falck Renewables SpA | Cambrian | Wind | Onshore | No | Wind |  | 58.5 | LV | Wales | Wales | SY233LE |  | 281000.0 | 280000.0 | 2005
Falck Renewables SpA | Earlsburn | Wind | Onshore | No | Wind |  | 37.5 | LV | Scotland | Scotland |  | NS697882 | 269652.0 | 688422.0 | 2007
Falck Renewables SpA | Kilbraur | Wind | Onshore | No | Wind |  | 67.5 | HV | Scotland | Scotland |  | NC788078 | 278550.0 | 907550.0 | 2008
Falck Renewables SpA | Kingsburn | Wind | Onshore | No | Wind |  | 22.5 | LV | Scotland | Scotland |  | NS668898 | 266606.0 | 686412.0 | 2016
Falck Renewables SpA | Millennium | Wind | Onshore | No | Wind |  | 65 | HV | Scotland | Scotland |  | NH265106 | 225679.0 | 810840.0 | 2008
Falck Renewables SpA | Nutberry | Wind | Onshore | No | Wind |  | 15 | LV | Scotland | Scotland |  | NS777322 | 279021.0 | 635662.0 | 2013
Falck Renewables SpA | Spaldington | Wind | Onshore | No | Wind |  | 11.75 | LV | England | Yorkshire and Humber |  | SE753329 | 475377.0 | 431986.0 | 2016
Falck Renewables SpA | West Browncastle | Wind | Onshore | No | Wind |  | 30 | LV | Scotland | Scotland |  | NS619426 | 261117.0 | 642821.0 | 2014
First Hydro Holdings Company | Cruachan | Pumped hydro | Pumped hydro | No | Pumped hydro |  | 440 | HV | Scotland | Scotland | PA331AN |  | 207006.0 | 716929.0 | 1965
First Hydro Holdings Company | Foyers Pumped Storage | Pumped hydro | Pumped hydro | No | Pumped hydro |  | 300 | HV | Scotland | Scotland |  | NH497210 | 250350.0 | 821750.0 | 1974
Foresight Group | Frodsham Wind Farm | Wind | Onshore | No | Wind |  | 50.35 | HV | England | North West | CH24LB |  | 348635.0 | 376504.0 | 2017
Foresight Group | Moel Moelogan | Wind | Onshore | No | Wind |  | 2.6 | HV | Wales | Wales |  |  | 284619.0 | 362203.0 | 2003
Foresight Group | Moel Moelogan 2 | Wind | Onshore | No | Wind |  | 11.7 | HV | Wales | Wales |  |  | 284700.0 | 361300.0 | 2008
Foresight Group | Shotwick | Solar | PV | No | Solar |  | 72.21 | LV | Wales | Wales | CH52UA |  | 332888.0 | 371036.0 | 2016
Fred Olsen Renewables | Brockloch Rig | Wind | Onshore | No | Wind |  | 61.5 | HV | Scotland | Scotland |  |  | 265160.0 | 596516.0 | 2017
Fred Olsen Renewables | Brockloch Rig 1 | Wind | Onshore | No | Wind |  | 21.6 | LV | Scotland | Scotland |  |  | 261500.0 | 602500.0 | 1996
Fred Olsen Renewables | Crystal Rig | Wind | Onshore | No | Wind |  | 62.5 | LV | Scotland | Scotland |  |  | 368000.0 | 667000.0 | 2003
Fred Olsen Renewables | Crystal Rig II | Wind | Onshore | No | Wind |  | 138 | HV | Scotland | Scotland |  |  | 367000.0 | 667500.0 | 2003
Fred Olsen Renewables | Crystal Rig III | Wind | Onshore | No | Wind |  | 13.8 | HV | Scotland | Scotland |  |  | 368562.0 | 672486.0 | 2016
Fred Olsen Renewables | Mid Hill | Wind | Onshore | No | Wind |  | 75.9 | LV | Scotland | Scotland |  |  | 370540.0 | 786500.0 | 2013
Fred Olsen Renewables | Pauls Hill | Wind | Onshore | No | Wind |  | 64.4 | LV | Scotland | Scotland |  |  | 311505.0 | 840495.0 | 2005
Fred Olsen Renewables | Rothes | Wind | Onshore | No | Wind |  | 50.6 | LV | Scotland | Scotland |  |  | 318400.0 | 855900.0 | 2004
Fred Olsen Renewables | Rothes II | Wind | Onshore | No | Wind |  | 41.4 | LV | Scotland | Scotland |  |  | 318500.0 | 850500.0 | 2013
Greencoat Capital | 30Acres | Solar | PV | No | Solar |  | 3.773 | LV | England | East Midlands | NG208XT |  | 453432.0 | 367916.0 | 2016
Greencoat Capital | Ainderby | Solar | PV | No | Solar |  | 4.961 | LV | England | Yorkshire and Humber | DL79PZ |  | 433420.0 | 492119.0 | 2017
Greencoat Capital | Arnawood | Solar | PV | No | Solar |  | 4.992 | LV | England | North West | LA20AE |  | 346363.0 | 459484.0 | 2017
Greencoat Capital | Ashby | Solar | PV | No | Solar |  | 4.7991 | LV | England | East Midlands | LE652UN |  | 434525.0 | 317774.0 | 2016
Greencoat Capital | Aston Clinton | Solar | PV | No | Solar |  | 24.2423 | LV | England | South East | HP225DY |  | 484594.0 | 215796.0 | 2015
Greencoat Capital | Bann Road | Solar | PV | No | Solar |  | 45.7528 | LV | Northern Ireland | Northern Ireland |  |  | 111262.0 | 571958.0 | 2017
Greencoat Capital | Bedborough | Solar | PV | No | Solar |  | 4.999 | LV | England | South West | BH217BQ |  | 404920.0 | 101836.0 | 2015
Greencoat Capital | Beech Farm | Solar | PV | No | Solar |  | 4.3027 | Distribution Network | England | South West | SN6 7SE |  |  |  | 2016
Greencoat Capital | Belper | Solar | PV | No | Solar |  | 4.9979 | LV | England | East Midlands | TS160PS |  | 437351.0 | 348648.0 | 2017
Greencoat Capital | Bent Spur | Solar | PV | No | Solar |  | 4.992 | LV | England | North West | BL48SJ |  | 375173.0 | 404114.0 | 2016
Greencoat Capital | Berthllwyd | Solar | PV | No | Solar |  | 4.9648 | LV | Wales | Wales | CF371PS |  | 307796.0 | 188016.0 | 2017
Greencoat Capital | Bicester | Solar | PV | No | Solar |  | 18.4 | LV | England | South East | OX252ND |  | 459052.0 | 218811.0 | 2013
Greencoat Capital | Bilsborrow | Solar | PV | No | Solar |  | 4.9926 | LV | England | North West | PR30RU |  | 350124.0 | 439100.0 | 2017
Greencoat Capital | Bin Mountain Wind Farm | Wind | Onshore | No | Wind |  | 9 | LV | Northern Ireland | Northern Ireland |  |  | 57145.0 | 558200.0 | 2007
Greencoat Capital | Bishopthorpe | Wind | Onshore | No | Wind |  | 16.4 | LV | England | East Midlands |  |  | 532679.0 | 403330.0 | 2017
Greencoat Capital | Bobbing | Solar | PV | No | Solar |  | 11.6012 | LV | England | South East | ME97HZ |  | 586894.0 | 165757.0 | 2016
Greencoat Capital | Bodwen | Solar | PV | No | Solar |  | 4.9998 | LV | England | South West | PL268RP |  | 202672.0 | 60536.0 | 2017
Greencoat Capital | Boganlea | Wind | Onshore | No | Wind |  | 2.31 | LV | Scotland | Scotland | AB535UY |  | 382155.0 | 852949.0 | 2014
Greencoat Capital | Braes of Doune Wind Farm | Wind | Onshore | No | Wind |  | 72 | HV | Scotland | Scotland |  |  | 272590.0 | 710500.0 | 2007
Greencoat Capital | Bransholme Solar | Solar | PV | No | Solar |  | 4.998 | LV | England | Yorkshire and Humber | HU75YX |  |  |  | 2016
Greencoat Capital | Brent Broad | Solar | PV | No | Solar |  | 3.7584 | LV | England | South West | BS246RR |  | 332623.0 | 152727.0 | 2017
Greencoat Capital | Brockaghboy | Wind | Onshore | No | Wind |  | 47.5 | LV | Northern Ireland | Northern Ireland |  |  | 96550.0 | 571846.0 | 2017
Greencoat Capital | Bryn Bachau | Solar | PV | No | Solar |  | 4.5721 | LV | Wales | Wales | LL536RQ |  | 243136.0 | 336998.0 | 2016
Greencoat Capital | BuryGreen | Solar | PV | No | Solar |  | 4.973 | LV | England | Eastern | PE262RY |  | 525500.0 | 285500.0 | 2016
Greencoat Capital | Carcant Wind Farm | Wind | Onshore | No | Wind |  | 6 | LV | Scotland | Scotland |  |  | 336250.0 | 652850.0 | 2010
Greencoat Capital | Carlam Hill Education | Solar | PV | No | Solar |  | 4.998 | LV | England | Yorkshire and Humber | HU75YX |  |  |  | 2016
Greencoat Capital | Carmarthen | Solar | PV | No | Solar |  | 4.7012 | LV | Wales | Wales | SA312LS |  | 0.0 | 0.0 | 2017
Greencoat Capital | Carn Nicholas | Solar | PV | No | Solar |  | 9.9 | Distribution Network | Wales | Wales | SA1 7BL |  |  |  | 2023
Greencoat Capital | Carnemough | Solar | PV | No | Solar |  | 10.1403 | LV | England | South West | TR24EL |  | 191629.0 | 52065.0 | 2016
Greencoat Capital | Carver Hey | Solar | PV | No | Solar |  | 2.5056 | LV | England | North West | PR44SX |  | 348519.0 | 423631.0 | 2017
Greencoat Capital | Christchurch | Solar | PV | No | Solar |  | 17.9266 | LV | England | South West | BH237AA |  | 417714.0 | 95129.0 | 2015
Greencoat Capital | Church Hill | Wind | Onshore | No | Wind |  | 18.4 | LV | Northern Ireland | Northern Ireland |  |  | 31711.0 | 543769.0 | 2012
Greencoat Capital | Clay Cross | Solar | PV | No | Solar |  | 4.9928 | LV | England | North West | CA141LG |  | 301000.0 | 532000.0 | 2017
Greencoat Capital | Cockett Valley | Solar | PV | No | Solar |  | 4.9993 | LV | Wales | Wales | SA54TH |  | 260884.0 | 195188.0 | 2017
Greencoat Capital | CommonFarm | Solar | PV | No | Solar |  | 3.3364 | LV | England | South West | SN49QJ |  | 413720.0 | 181837.0 | 2017
Greencoat Capital | Coombe | Solar | PV | No | Solar |  | 7.2785 | LV | England | South West | EX85AZ |  | 301187.0 | 84681.0 | 2015
Greencoat Capital | Corriegarth | Wind | Onshore | No | Wind |  | 69.5 | HV | Scotland | Scotland |  |  | 257500.0 | 813500.0 | 2017
Greencoat Capital | Cotton Farm | Wind | Onshore | No | Wind |  | 16.4 | LV | England | Eastern |  |  | 523270.0 | 264130.0 | 2013
Greencoat Capital | Crighshane | Wind | Onshore | No | Wind |  | 32.2 | HV | Northern Ireland | Northern Ireland |  |  | 29021.0 | 542409.0 | 2012
Greencoat Capital | Douglas West | Wind | Onshore | No | Wind |  | 44.85 | LV | Scotland | Scotland | ML11 0FW |  |  |  | 2021
Greencoat Capital | Dove View | Solar | PV | No | Solar |  | 4.5652 | Distribution Network | England | West Midlands | ST14 8JY |  |  |  | 2016
Greencoat Capital | Drone Hill | Wind | Onshore | No | Wind |  | 28.6 | LV | Scotland | Scotland |  |  | 383719.0 | 667227.0 | 2012
Greencoat Capital | Earls Hall Farm | Wind | Onshore | No | Wind |  | 10.25 | LV | England | Eastern |  |  | 614550.0 | 216860.0 | 2013
Greencoat Capital | Ebnal Lodge | Solar | PV | No | Solar |  | 4.9894 | LV | England | West Midlands | SY107BL |  | 331810.0 | 334117.0 | 2017
Greencoat Capital | Egmanton | Solar | PV | No | Solar |  | 14.1085 | LV | England | East Midlands | NG220HH |  |  |  | 2015
Greencoat Capital | Errol | Solar | PV | No | Solar |  | 12.9994 | LV | Scotland | Scotland | PH27NL |  | 321840.0 | 721031.0 | 2016
Greencoat Capital | Eveley | Solar | PV | No | Solar |  | 49.328 | LV | England | South East | SO206SA |  | 432815.0 | 133266.0 | 2016
Greencoat Capital | FannyHouse | Solar | PV | No | Solar |  | 4.942 | LV | England | North West | LA33EF |  | 342598.0 | 462146.0 | 2015
Greencoat Capital | Ferry Farm | Solar | PV | No | Solar |  | 4.924 | LV | England | South East | PO209DZ |  | 485830.0 | 96047.0 | 2015
Greencoat Capital | Flit | Solar | PV | No | Solar |  | 10.4652 | LV | England | South East | OX51PH |  |  |  | 2015
Greencoat Capital | Gaultney | Solar | PV | No | Solar |  | 21.558 | LV | England | East Midlands | NN142SW |  |  |  | 2015
Greencoat Capital | Gedulah | Solar | PV | No | Solar |  | 18.33 | LV | England | North West | CA73JU |  |  |  | 2015
Greencoat Capital | Glen Kyllachy | Wind | Onshore | No | Wind |  | 48.5 | HV | England | Scotland |  |  |  |  | 2021
Greencoat Capital | GrangeFarm | Solar | PV | No | Solar |  | 5.8022 | LV | England | South East | TA210BU |  | 229006.0 | 92956.0 | 2013
Greencoat Capital | Henley | Solar | PV | No | Solar |  | 4.999 | LV | England | West Midlands | SY66RS |  | 345599.0 | 288062.0 | 2017
Greencoat Capital | Homestead | Solar | PV | No | Solar |  | 17.7125 | LV | England | South East | NN127LS |  | 473845.0 | 244756.0 | 2015
Greencoat Capital | Honeysome | Solar | PV | No | Solar |  | 4.346 | LV | England | Eastern | PE166TG |  | 538755.0 | 286122.0 | 2016
Greencoat Capital | Hoplass | Solar | PV | No | Solar |  | 10.3428 | LV | Wales | Wales | SA715TG |  | 190875.0 | 200362.0 | 2015
Greencoat Capital | Hunger Hill | Solar | PV | No | Solar |  | 4.9958 | LV | England | North East | DL21JZ |  | 433439.0 | 512522.0 | 2017
Greencoat Capital | Huntspill | Solar | PV | No | Solar |  | 4.993 | LV | England | South West | TA93PN |  | 332877.0 | 144342.0 | 2016
Greencoat Capital | Hurcott | Solar | PV | No | Solar |  | 9.9965 | Distribution Network | England | South West | TA19 0JS |  |  |  | 2015
Greencoat Capital | Islip | Solar | PV | No | Solar |  | 4.9912 | LV | England | East Midlands | NN143LT |  | 497983.0 | 279596.0 | 2012
Greencoat Capital | Kildrummy | Wind | Onshore | No | Wind |  | 18.4 | LV | Scotland | Scotland |  |  | 357655.0 | 815170.0 | 2013
Greencoat Capital | Kinmel 1 | Solar | PV | No | Solar |  | 4.9986 | LV | Wales | Wales | LL229SD |  |  |  | 2016
Greencoat Capital | Kinmel 2 | Solar | PV | No | Solar |  | 4.992 | LV | Wales | Wales | LL229SG |  |  |  | 2016
Greencoat Capital | Lagness | Solar | PV | No | Solar |  | 4.847 | LV | England | South East | PO201LR |  | 490675.0 | 101234.0 | 2016
Greencoat Capital | Langhope Rig | Wind | Onshore | No | Wind |  | 16.4 | LV | Scotland | Scotland |  |  | 340519.0 | 615032.0 | 2013
Greencoat Capital | Laurel Hill | Solar | PV | No | Solar |  | 14.202 | LV | England | Northern Ireland | BT251JS |  |  |  | 2018
Greencoat Capital | Limberlost | Solar | PV | No | Solar |  | 1.594 | LV | England | South East | RG198BR |  | 453510.0 | 164953.0 | 2013
Greencoat Capital | Llancayo | Solar | PV | No | Solar |  | 4.91 | LV | Wales | Wales | NP151HY |  | 336790.0 | 203067.0 | 2011
Greencoat Capital | Long Meadow | Solar | PV | No | Solar |  | 4.1198 | LV | England | South East | LU79DY |  | 493475.0 | 217559.0 | 2015
Greencoat Capital | LowerHouse | Solar | PV | No | Solar |  | 8.2237 | LV | Wales | Wales | NP151JU |  | 334870.0 | 204817.0 | 2016
Greencoat Capital | Maerdy | Wind | Onshore | No | Wind |  | 24 | LV | Wales | Wales |  |  | 295390.0 | 199853.0 | 2013
Greencoat Capital | Manor Farm | Solar | PV | No | Solar |  | 4.869 | LV | England | South West | P0229NR |  | 355189.0 | 130227.0 | 2011
Greencoat Capital | Marchington | Solar | PV | No | Solar |  | 4.9982 | LV | England | West Midlands | DE65GX |  |  |  | 2016
Greencoat Capital | Margate | Solar | PV | No | Solar |  | 3.366 | LV | England | South West | PL311HE |  | 208657.0 | 66512.0 | 2015
Greencoat Capital | Merston | Solar | PV | No | Solar |  | 4.999 | LV | England | South East | PO201LL |  | 489440.0 | 102825.0 | 2016
Greencoat Capital | Moat Farm | Solar | PV | No | Solar |  | 4.6176 | LV | England | East Midlands | DN228QX |  | 466600.0 | 384353.0 | 2015
Greencoat Capital | Mount Farm | Solar | PV | No | Solar |  | 23.0789 | LV | England | [5 empty] | 2016
Greencoat Capital | Netley | Solar | PV | No | Solar |  | 4.997 | LV | England | South East | SO315FF |  | 446625.0 | 109005.0 | 2017
Greencoat Capital | New Kaine | Solar | PV | No | Solar |  | 1.8748 | LV | England | South East | ME97HP |  | 584858.0 | 166460.0 | 2015
Greencoat Capital | North Rhins | Wind | Onshore | No | Wind |  | 22 | LV | Scotland | Scotland |  |  | 201980.0 | 557960.0 | 2009
Greencoat Capital | Pantymoch | Solar | PV | No | Solar |  | 4.992 | LV | Wales | Wales | SA132UT |  | 277876.0 | 190467.0 | 2016
Greencoat Capital | Pantymoch CIC | Solar | PV | No | Solar |  | 4.896 | LV | Wales | Wales | SA132UT |  | 277876.0 | 190467.0 | 2016
Greencoat Capital | Potters Bar | Solar | PV | No | Solar |  | 4.9981 | LV | England | Eastern | EN63DQ |  | 524112.0 | 202677.0 | 2017
Greencoat Capital | Radstone | Solar | PV | No | Solar |  | 5.2204 | LV | England | East Midlands | NN135PY |  |  |  | 2015
Greencoat Capital | RamseySolar | Solar | PV | No | Solar |  | 4.973 | LV | England | Eastern | PE262RU |  | 527862.0 | 284726.0 | 2016
Greencoat Capital | Redbridge | Solar | PV | No | Solar |  | 6.4832 | LV | England | South West | DT28DY |  | 377194.0 | 88984.0 | 2013
Greencoat Capital | Rhewl 1 | Solar | PV | No | Solar |  | 3.0415 | LV | Wales | Wales | NP166AG |  |  |  | 2016
Greencoat Capital | Rhewl 2 | Solar | PV | No | Solar |  | 3.0716 | LV | Wales | Wales | NP166AG |  |  |  | 2016
Greencoat Capital | Rolleston | Solar | PV | No | Solar |  | 18.003 | LV | England | West Midlands | DE139HH |  | 421291.0 | 326955.0 | 2015
Greencoat Capital | Rose & Crown | Solar | PV | No | Solar |  | 30.107 | LV | England | [5 empty] | 2016
Greencoat Capital | Rowles | Solar | PV | No | Solar |  | 12.762 | LV | England | South East | OX253QQ |  |  |  | 2015
Greencoat Capital | Royston | Solar | PV | No | Solar |  | 4.96 | LV | England | Eastern | SG85UT |  | 535667.0 | 242584.0 | 2016
Greencoat Capital | Royston CIC | Solar | PV | No | Solar |  | 4.896 | LV | England | Eastern | SG85UT |  | 535667.0 | 242584.0 | 2016
Greencoat Capital | Sandhutton | Solar | PV | No | Solar |  | 4.9998 | LV | England | Yorkshire and Humber | YO74RW |  | 439302.0 | 482532.0 | 2017
Greencoat Capital | Saron | Solar | PV | No | Solar |  | 6.3326 | LV | Wales | Wales | SA183TW |  | 260904.0 | 212664.0 | 2015
Greencoat Capital | ScottowMoor | Solar | PV | No | Solar |  | 33.68 | LV | England | Eastern | NR105FB |  | 626488.0 | 323770.0 | 2015
Greencoat Capital | Screggagh | Wind | Onshore | No | Wind |  | 20 | LV | Northern Ireland | Northern Ireland |  |  | 54566.0 | 520549.0 | 2011
Greencoat Capital | Seaview | Solar | PV | No | Solar |  | 1.8774 | LV | Wales | Wales | CF365TB |  | 282388.0 | 178878.0 | 2016
Greencoat Capital | Sellindge | Solar | PV | No | Solar |  | 11.2093 | LV | England | South East | TN256EE |  | 608480.0 | 137870.0 | 2016
Greencoat Capital | Severn Beach | Solar | PV | No | Solar |  | 3.9562 | LV | England | South West | BS354NL |  | 354534.0 | 184909.0 | 2016
Greencoat Capital | Sixpenny Wood | Wind | Onshore | No | Wind |  | 20.5 | LV | England | Yorkshire and Humber |  |  | 478500.0 | 427500.0 | 2013
Greencoat Capital | Slade Farm | Solar | PV | No | Solar |  | 4.0966 | LV | England | South West | TQ72HE |  | 274224.0 | 45194.0 | 2015
Greencoat Capital | Slieve Divena | Wind | Onshore | No | Wind |  | 30 | LV | Northern Ireland | Northern Ireland |  |  | 69602.0 | 524593.0 | 2009
Greencoat Capital | Slieve Divena 2 | Wind | Onshore | No | Wind |  | 18.8 | LV | Northern Ireland | Northern Ireland |  |  | 69602.0 | 524593.0 | 2017
Greencoat Capital | SMSL1 | Solar | PV | No | Solar |  | 4.7696 | LV | England | Eastern | NR105FB |  | 626626.0 | 322780.0 | 2016
Greencoat Capital | SMSL2 | Solar | PV | No | Solar |  | 4.8905 | LV | England | Eastern | NR105FB |  | 625975.0 | 323016.0 | 2016
Greencoat Capital | SMSL3 | Solar | PV | No | Solar |  | 4.9524 | LV | England | Eastern | NR105FB |  | 625975.0 | 323016.0 | 2016
Greencoat Capital | SMSL4 | Solar | PV | No | Solar |  | 3.6445 | LV | England | Eastern | NR105FB |  | 625975.0 | 323016.0 | 2016
Greencoat Capital | Snettisham | Solar | PV | No | Solar |  | 2.6928 | LV | England | Eastern | PE317NE |  | 570621.0 | 334187.0 | 2017
Greencoat Capital | Springhill | Solar | PV | No | Solar |  | 4.9477 | LV | England | South West | WR127LB |  | 413653.0 | 235615.0 | 2011
Greencoat Capital | Stables | Solar | PV | No | Solar |  | 1.966 | LV | England | East Midlands | CV136EB |  | 440233.0 | 297103.0 | 2014
Greencoat Capital | Stonebarrow | Solar | PV | No | Solar |  | 7.485 | LV | England | South West | EX135UL |  | 334899.0 | 98840.0 | 2014
Greencoat Capital | Streetfueld | Solar | PV | No | Solar |  | 49.9875 | Distribution Network | England | West Midlands | LE17 4HS |  |  |  | 2023
Greencoat Capital | Stroupster | Wind | Onshore | No | Wind |  | 29.9 | LV | Scotland | Scotland |  |  | 334250.0 | 966250.0 | 2015
Greencoat Capital | Sudbrook | Solar | PV | No | Solar |  | 4.998 | LV | Wales | Wales | NP265SR |  | 350024.0 | 187852.0 | 2016
Greencoat Capital | Tappaghan Wind Farm | Wind | Onshore | No | Wind |  | 28.5 | LV | Northern Ireland | Northern Ireland |  |  | 41015.0 | 531174.0 | 2005
Greencoat Capital | Thornham | Solar | PV | No | Solar |  | 20.627 | LV | England | East | PE365LH |  |  |  | 2022
Greencoat Capital | Tom Nan Clach | Wind | Onshore | No | Wind |  | 39.1 | HV | Scotland | Scotland |  |  | 286500.0 | 834500.0 | 2019
Greencoat Capital | Trefullock | Solar | PV | No | Solar |  | 4.9979 | LV | England | South West | TR85BH |  |  |  | 2011
Greencoat Capital | Turweston | Solar | PV | No | Solar |  | 16.4448 | Distribution Network | England | South East | NN13 5YD |  |  |  | 2014
Greencoat Capital | TwentyShilling Hill | Wind | Onshore | No | Wind |  | 37.8 | Transmission Network | Scotland | Scotland |  |  |  |  | 2022
Greencoat Capital | Upper Meadowley | Solar | PV | No | Solar |  | 4.8654 | LV | England | West Midlands | WV166UQ |  | 366792.0 | 292516.0 | 2017
Greencoat Capital | Vine Farm | Solar | PV | No | Solar |  | 45.916 | LV | England | South East |  |  |  |  | 2016
Greencoat Capital | West Carclaze | Solar | PV | No | Solar |  | 4.9948 | LV | England | South West | PL268XL |  | 201930.0 | 55161.0 | 2017
Greencoat Capital | West Strathore | Solar | PV | No | Solar |  | 4.9773 | LV | Scotland | Scotland | KY14DQ |  | 328619.0 | 697504.0 | 2017
Greencoat Capital | Westover | Solar | PV | No | Solar |  | 7.0416 | LV | England | South East | SP117SE |  | 434623.0 | 140438.0 | 2014
Greencoat Capital | Wick Road | Solar | PV | No | Solar |  | 4.6627 | LV | England | South West | BS246RR |  | 331664.0 | 154677.0 | 2016
Greencoat Capital | Wick Road CIC | Solar | PV | No | Solar |  | 2.1994 | LV | England | South West | BS246RR |  | 331664.0 | 154677.0 | 2016
Greencoat Capital | Wilsom Farm | Solar | PV | No | Solar |  | 4.0058 | LV | England | South East | GU343BF |  | 472777.0 | 138856.0 | 2016
Greencoat Capital | Wilton | Solar | PV | No | Solar |  | 9.4838 | LV | England | South West | PL125BX |  | 231509.0 | 58873.0 | 2015
Greencoat Capital | Windy Rig | Wind | Onshore | No | Wind |  | 43.2 | HV | England | Scotland |  |  |  |  | 2021
Greencoat Capital | Wrangle | Solar | PV | No | Solar |  | 10.795 | LV | England | East Midlands | PE220PZ |  | 538495.0 | 348945.0 | 2014
Greencoat Capital | Wraysbury | Solar | PV | No | Solar |  | 3.049 | LV | England | South East | TW195AH |  | 501492.0 | 172752.0 | 2017
Greencoat Capital | Yelvertoft | Wind | Onshore | No | Wind |  | 16.4 | LV | England | East Midlands |  |  | 457887.0 | 275532.0 | 2013
Intergen | Coryton Energy Company Ltd | Fossil Fuel | CCGT | No | Natural Gas |  | 800 | HV | England | South East |  |  | 565166.0 | 178798.0 | 2002
Intergen | Rocksavage Power Company Ltd | Fossil Fuel | CCGT | No | Natural Gas |  | 810 | HV | England | North West |  |  | 352414.0 | 377661.0 | 1998
Intergen | Spalding Energy Company | Fossil Fuel | CCGT | No | Natural Gas |  | 950 | HV | England | East Midlands |  |  | 524944.0 | 320245.0 | 2004
Intergen | Spalding Expansion OCGT | Fossil Fuel | Single cycle | No | Natural Gas |  | 300 | HV | England | East Midlands | PE11 3BB |  |  |  | 2019
Kentish Flats Ltd | South Kyle | Wind | Onshore | No | Wind |  | 240 |  | Scotland | Scotland |  |  | 254849 | 604654 | 2023
Lightsource BP | Acrefair | Solar | PV | No | Solar |  | 4.997 | LV | Wales | Wales | LL141TU |  | 328224.0 | 343948.0 | 2015
Lightsource BP | Beckton | Solar | PV | No | Solar |  | 0.45264 | LV | England | London | IG110AD |  | 545350.0 | 181950.0 | 2016
Lightsource BP | Benbole | Solar | PV | No | Solar |  | 1.739 | LV | England | South West | PL303EF |  | 202931.0 | 74850.0 | 2011
Lightsource BP | Bentley Estate | Solar | PV | No | Solar |  | 4.7819 | LV | England | South East | BN86PT |  | 548420.0 | 117019.0 | 2015
Lightsource BP | Bentley Estate 2 | Solar | PV | No | Solar |  | 4.9961 | LV | England | South East | BN86PT |  | 548465.0 | 117641.0 | 2016
Lightsource BP | Binsted | Solar | PV | No | Solar |  | 4.9979 | LV | England | South East | BN180LN |  | 498131.0 | 106406.0 | 2016
Lightsource BP | Blatchworthy | Solar | PV | No | Solar |  | 1.4125 | LV | England | South West |  | EX169QH | 250572.0 | 140713.0 | 2013
Lightsource BP | Bodmin | Solar | PV | No | Solar |  | 4.9768 | LV | England | South West | PL312PF |  | 206175.0 | 68428.0 | 2012
Lightsource BP | Bolsovermoor Quarry | Solar | PV | No | Solar |  | 4.9979 | LV | England | East Midlands | S446XE |  | 449954.0 | 371271.0 | 2017
Lightsource BP | Brett Martin | Solar | PV | No | Solar |  | 6.4858 | LV | Northern Ireland | Northern Ireland | BT364QU |  | 141191.0 | 538562.0 | 2018
Lightsource BP | Brook Farm | Solar | PV | No | Solar |  | 8.9104 | LV | England | South East | OX251NX |  | 461083.0 | 217119.0 | 2015
Lightsource BP | Brynteg | Solar | PV | No | Solar |  | 14.7866 | LV | Wales | Wales | SA154ND |  | 249621.0 | 203809.0 | 2014
Lightsource BP | Burnthouse | Solar | PV | No | Solar |  | 4.7624 | LV | England | Eastern | PE72HS |  | 534234.0 | 294198.0 | 2014
Lightsource BP | Burthy | Solar | PV | No | Solar |  | 13.0804 | LV | England | South West | TR85BN |  | 191082.0 | 55525.0 | 2015
Lightsource BP | Bury Lane | Solar | PV | No | Solar |  | 22.2159 | LV | England | Eastern | SG86DF |  | 537439.0 | 244200.0 | 2014
Lightsource BP | Castle Combe | Solar | PV | No | Solar |  | 15.3274 | LV | England | South West | SN147EY |  | 385003.0 | 177211.0 | 2015
Lightsource BP | Charity Farm - CfD | Solar | PV | No | Solar |  | 14.4025 | LV | England | West Midlands | SY45SX |  | 345545.0 | 325520.0 | 2016
Lightsource BP | Chittering | Solar | PV | No | Solar |  | 4.9934 | LV | England | Eastern |  |  | 551488.0 | 271214.0 | 2012
Lightsource BP | Church Farm - Slapton | Solar | PV | No | Solar |  | 4.9848 | LV | England | South East | LU79DY |  | 494241.0 | 220134.0 | 2015
Lightsource BP | Cleave Farm | Solar | PV | No | Solar |  | 4.5644 | LV | England | South West | EX394PU |  | 249891.0 | 124902.0 | 2013
Lightsource BP | Cold Harbour | Solar | PV | No | Solar |  | 5 | LV | England | Yorkshire and Humber | YO73NT |  | 444776.0 | 475104.0 | 2015
Lightsource BP | Crookedstone | Solar | PV | No | Solar |  | 4.8318 | LV | Northern Ireland | Northern Ireland | BT294EH |  | 129401.0 | 538723.0 | 2016
Lightsource BP | Crossness | Solar | PV | No | Solar |  | 1.5037 | LV | England | London | SE29AQ |  | 548450.0 | 180950.0 | 2011
Lightsource BP | Crucis Farm | Solar | PV | No | Solar |  | 16.057 | LV | England | South West | GL75DX |  | 406095.0 | 202822.0 | 2014
Lightsource BP | Crundale | Solar | PV | No | Solar |  | 43.6643 | LV | Wales | Wales | SA624PY |  | 198922.0 | 217459.0 | 2015
Lightsource BP | Cwrt Henllys | Solar | PV | No | Solar |  | 4.9925 | LV | Wales | Wales | NP447AS |  | 326262.0 | 191423.0 | 2016
Lightsource BP | Dunsfold | Solar | PV | No | Solar |  | 2.0006 | LV | England | South East |  |  | 501944.09999999998 | 136562.0 | 2011
Lightsource BP | Eastacombe | Solar | PV | No | Solar |  | 3.577 | LV | England | South West |  |  | 235435.0 | 99648.0 | 2012
Lightsource BP | Epwell | Solar | PV | No | Solar |  | 8.988 | LV | England | South East | OX156HF |  | 436715.0 | 241041.0 | 2014
Lightsource BP | Exning | Solar | PV | No | Solar |  | 30.276 | LV | England | Eastern | CB80XG |  | 561429.0 | 263931.0 | 2015
Lightsource BP | Fairwinds | Solar | PV | No | Solar |  | 12.1969 | LV | England | Eastern | SS166EB |  | 565725.0 | 187731.0 | 2014
Lightsource BP | Fareham | Solar | PV | No | Solar |  | 20.508 | LV | England | South East | PO141AU |  | 456710.0 | 103840.0 | 2014
Lightsource BP | Fawley (Langley) | Solar | PV | No | Solar |  | 4.9997 | LV | England | South East | SO451AB |  | 445171.0 | 100816.0 | 2012
Lightsource BP | Ffos Las | Solar | PV | No | Solar |  | 4.9968 | LV | Wales | Wales |  |  | 245478.0 | 205296.0 | 2012
Lightsource BP | Fields Farm (Agden) | Solar | PV | No | Solar |  | 4.9975 | LV | England | North West | SY134RB |  | 351085.0 | 344240.0 | 2017
Lightsource BP | Finvoy | Solar | PV | No | Solar |  | 5.9609 | LV | Northern Ireland | Northern Ireland | BT448SD |  | 112523.0 | 572478.0 | 2017
Lightsource BP | Five Mile Drive | Solar | PV | No | Solar |  | 3.912 | LV | England | South West | GL569TG |  | 413600.0 | 235700.0 | 2013
Lightsource BP | Francis Court | Solar | PV | No | Solar |  | 4.224 | LV | England | South West | EX53LW |  | 297957.0 | 99694.0 | 2015
Lightsource BP | Gelli Gron | Solar | PV | No | Solar |  | 3.597 | LV | Wales | Wales | LL536DQ |  | 241787.0 | 339725.0 | 2016
Lightsource BP | Goosehall | Solar | PV | No | Solar |  | 43.2216 | LV | England | Eastern | CB250BN |  |  |  | 2020
Lightsource BP | Great Knowles | Solar | PV | No | Solar |  | 2.915 | LV | England | South West | EX226JY |  | 232612.0 | 103213.0 | 2012
Lightsource BP | Green Lane | Solar | PV | No | Solar |  | 4.2299 | LV | England | West Midlands | ST148LQ |  | 414839.0 | 330919.0 | 2017
Lightsource BP | Hadley Farm | Solar | PV | No | Solar |  | 4.997 | LV | England | West Midlands | SY133AB |  | 351460.0 | 340636.0 | 2015
Lightsource BP | Hawton | Solar | PV | No | Solar |  | 4.877 | LV | England | East Midlands | NG243RJ |  | 479632.0 | 348905.0 | 2011
Lightsource BP | Henbury Quarry | Solar | PV | No | Solar |  | 3.684 | LV | England | South West | BH213QZ |  | 396735.0 | 97102.0 | 2015
Lightsource BP | High Point | Solar | PV | No | Solar |  | 3.7484 | LV | England | West Midlands | DY149AD |  | 366415.0 | 270925.0 | 2017
Lightsource BP | Hill Farm | Solar | PV | No | Solar |  | 7.6934 | LV | Wales | Wales | NP117BB |  | 319254.0 | 192650.0 | 2015
Lightsource BP | Hill Hall Farm | Solar | PV | No | Solar |  | 4.999 | LV | England | Eastern | CM74SH |  | 565650.0 | 232265.0 | 2016
Lightsource BP | Hill House Farm | Solar | PV | No | Solar |  | 28.3118 | LV | England | South West | GL27AN |  | 375073.0 | 204169.0 | 2015
Lightsource BP | Horam | Solar | PV | No | Solar |  | 8.1151 | LV | England | South East | TN210JB |  | 557342.0 | 117038.0 | 2015
Lightsource BP | Hornacott | Solar | PV | No | Solar |  | 4.997 | LV | England | South West | EX226SD |  | 230097.0 | 95148.0 | 2015
Lightsource BP | Howbery | Solar | PV | No | Solar |  | 0.7485 | LV | England | South East | TR24EP |  | 461755.0 | 190325.0 | 2011
Lightsource BP | Howton | Solar | PV | No | Solar |  | 4.9997 | LV | England | South West | PL126QY |  | 238063.0 | 62770.0 | 2011
Lightsource BP | Ibstock | Solar | PV | No | Solar |  | 4.8196 | LV | England | West Midlands |  | LE676HS |  |  | 2020
Lightsource BP | Knowlton | Solar | PV | No | Solar |  | 11.541 | LV | England | South East | CT31PT |  | 628013.0 | 153474.0 | 2014
Lightsource BP | Langton (FIT) | Solar | PV | No | Solar |  | 4.3472 | LV | Wales | Wales | SA659RH |  | 194473.0 | 233813.0 | 2015
Lightsource BP | Langunnett | Solar | PV | No | Solar |  | 6.174 | LV | England | South West | PL220NQ |  | 215569.0 | 57824.0 | 2013
Lightsource BP | Lawrence End Park | Solar | PV | No | Solar |  | 5 | LV | England | Eastern | LU28PF |  | 513149.0 | 220690.0 | 2015
Lightsource BP | Little Neath | Solar | PV | No | Solar |  | 6.135 | LV | Wales | Wales | SA715AA |  | 191001.0 | 200291.0 | 2015
Lightsource BP | Maes Bach | Solar | PV | No | Solar |  | 4.5594 | LV | Wales | Wales | CF381SL |  | 310571.0 | 185789.0 | 2015
Lightsource BP | Maghaberry | Solar | PV | No | Solar |  | 27.099 | LV | Northern Ireland | Northern Ireland | BT282PT |  | 129097.0 | 520344.0 | 2018
Lightsource BP | Manor Farm | Solar | PV | No | Solar |  | 0.7636 | LV | England | South West | TA117BT |  | 493450.0 | 102216.0 | 2016
Lightsource BP | Manston | Solar | PV | No | Solar |  | 9.831 | LV | England | South East | CT125AU |  | 634574.0 | 166813.0 | 2013
Lightsource BP | Marston | Solar | PV | No | Solar |  | 4.5114 | LV | England | East Midlands | NG322JP |  | 488029.0 | 342114.0 | 2011
Lightsource BP | Meadow Farm (Thorpe Lanton) | Solar | PV | No | Solar |  | 4.998 | LV | England | East Midlands | LE167TR |  | 472795.0 | 290643.0 | 2017
Lightsource BP | Middle Balbeggie | Solar | PV | No | Solar |  | 4.9975 | LV | Scotland | Scotland | KY13NW |  | 328584.0 | 696136.0 | 2017
Lightsource BP | Millar Farm | Solar | PV | No | Solar |  | 7.2109 | LV | Northern Ireland | Northern Ireland | BT412JJ |  | 127283.0 | 546753.0 | 2017
Lightsource BP | Moor Solar 1 | Solar | PV | No | Solar |  | 1.6666 | LV | England | East Midlands |  |  | 544055.0 | 323522.0 | 2011
Lightsource BP | Moor Solar 2 | Solar | PV | No | Solar |  | 1.0675 | LV | England | East Midlands |  |  | 544125.0 | 323559.0 | 2011
Lightsource BP | Morfa | Solar | PV | No | Solar |  | 1.999 | LV | Wales | Wales | CF612YT |  | 258062.0 | 301195.0 | 2016
Lightsource BP | Nefyn (Tyddyn Cae) | Solar | PV | No | Solar |  | 4.9215 | LV | Wales | Wales | LL536DS |  | 233416.0 | 338035.0 | 2015
Lightsource BP | NI Cluster Belfast Road | Solar | PV | No | Solar |  | 9.9919 | LV | Northern Ireland | Northern Ireland | BT294TH |  | 134568.0 | 534503.0 | 2017
Lightsource BP | NI Cluster Hillside | Solar | PV | No | Solar |  | 5.399 | LV | Northern Ireland | Northern Ireland | BT282PQ |  | 129820.0 | 526363.0 | 2017
Lightsource BP | NI Cluster Knockairn Road | Solar | PV | No | Solar |  | 5.3985 | LV | Northern Ireland | Northern Ireland | BT294UE |  | 131013.0 | 531722.0 | 2017
Lightsource BP | NI Cluster Lough Road | Solar | PV | No | Solar |  | 5.399 | LV | Northern Ireland | Northern Ireland | BT282PQ |  | 129148.0 | 526209.0 | 2017
Lightsource BP | NI Cluster Moira Road | Solar | PV | No | Solar |  | 5.9371 | LV | Northern Ireland | Northern Ireland | BT294JL |  | 129536.0 | 531688.0 | 2017
Lightsource BP | NOR Parsonage Wood | Solar | PV | No | Solar |  | 4.1835 | LV | England | South West | EX226LA |  | 231095.0 | 102160.0 | 2017
Lightsource BP | Norrington | Solar | PV | No | Solar |  | 11.145 | LV | England | South West | SN128LT |  | 388259.0 | 164933.0 | 2014
Lightsource BP | North Tenement | Solar | PV | No | Solar |  | 4.9979 | LV | Wales | Wales | SA623NX |  | 193951.0 | 212945.0 | 2017
Lightsource BP | Park Farm West | Solar | PV | No | Solar |  | 3.9348 | LV | Wales | Wales | NP183NY |  | 331876.0 | 191657.0 | 2017
Lightsource BP | Pen Rhiw | Solar | PV | No | Solar |  | 4.748 | LV | Wales | Wales | CF453UX |  | 304596.0 | 197986.0 | 2017
Lightsource BP | Pilkington | Solar | PV | No | Solar |  | 2.2968 | LV | England | North West | L407TB |  | 346150.0 | 408856.0 | 2019
Lightsource BP | Pont Andrew | Solar | PV | No | Solar |  | 1.5443 | LV | Wales | Wales | CF449UL |  | 252617.0 | 210675.0 | 2012
Lightsource BP | Pressock | Solar | PV | No | Solar |  | 4.249 | LV | Scotland | Scotland | DD82SN |  | 356791.0 | 749786.0 | 2017
Lightsource BP | Prestop Park | Solar | PV | No | Solar |  | 15.852 | LV | England | East Midlands | LE652TE |  | 433582.0 | 316633.0 | 2015
Lightsource BP | Primrose Hill | Solar | PV | No | Solar |  | 4.3452 | LV | England | Yorkshire and Humber | LN85JE |  | 460491.0 | 428957.0 | 2015
Lightsource BP | Promens | Solar | PV | No | Solar |  | 1.6485 | LV | England | Eastern | NR347TB |  | 644496.0 | 288255.0 | 2011
Lightsource BP | QE2 Reservoir | Solar | PV | No | Solar |  | 6.3377 | LV | England | South East | IG110AD |  | 512509.0 | 167686.0 | 2016
Lightsource BP | RedHill Farm | Solar | PV | No | Solar |  | 4.7976 | LV | England | South West | TA210DL |  | 308588.0 | 118087.0 | 2015
Lightsource BP | Rudge Hill Farm | Solar | PV | No | Solar |  | 1.0189 | LV | England | South West | DT102AB |  | 378118.0 | 112656.0 | 2013
Lightsource BP | Safeguard Bradwall | Solar | PV | No | Solar |  | 4.9975 | LV | England | North West | CW100LA |  | 375914.0 | 363479.0 | 2017
Lightsource BP | Sandhill | Solar | PV | No | Solar |  | 1.9228 | LV | England | South West |  |  | 316188.0 | 129704.0 | 2011
Lightsource BP | Says Court | Solar | PV | No | Solar |  | 19.807 | LV | England | South West | BS362NY |  | 368922.0 | 181730.0 | 2014
Lightsource BP | School Aycliffe | Solar | PV | No | Solar |  | 5 | LV | England | North East | DL56QE |  | 426142.0 | 523694.0 | 2015
Lightsource BP | Shaftesbury | Solar | PV | No | Solar |  | 4.997 | LV | England | South West | SP79HD |  | 386849.0 | 124179.0 | 2015
Lightsource BP | Sharland Farm | Solar | PV | No | Solar |  | 2.7711 | LV | England | South West | EX176SJ |  | 274885.0 | 105456.0 | 2017
Lightsource BP | Sheriffhales | Solar | PV | No | Solar |  | 5 | LV | England | West Midlands | TF118QY |  | 375171.0 | 312179.0 | 2015
Lightsource BP | South Creake | Solar | PV | No | Solar |  | 26.0012 | LV | England | Eastern | NR219LY |  | 585483.0 | 335992.0 | 2016
Lightsource BP | St Francis | Solar | PV | No | Solar |  | 4.3253 | LV | England | South East | TN339BL |  | 572709.0 | 111249.0 | 2015
Lightsource BP | Stragglethorpe | Solar | PV | No | Solar |  | 4.9993 | LV | England | East Midlands | NG123HD |  | 463188.0 | 336136.0 | 2016
Lightsource BP | Summerlands | Solar | PV | No | Solar |  | 0.8064 | LV | England | South West | EX174DF |  | 284552.0 | 108297.0 | 2012
Lightsource BP | Sundorne Grove | Solar | PV | No | Solar |  | 18.226 | LV | England | West Midlands | SY44RR |  | 352826.0 | 315367.0 | 2015
Lightsource BP | Trefinnick | Solar | PV | No | Solar |  | 4.4036 | LV | England | South West | PL178QD |  | 233642.0 | 74030.0 | 2013
Lightsource BP | Treguff | Solar | PV | No | Solar |  | 3.7365 | LV | Wales | Wales | CF715LT |  | 302265.0 | 171141.0 | 2015
Lightsource BP | Trevemper | Solar | PV | No | Solar |  | 1.6999 | LV | England | South West |  |  | 181946.0 | 59506.0 | 2011
Lightsource BP | Upper Clayhill | Solar | PV | No | Solar |  | 4.7492 | LV | England | South East | BN85RR |  | 544648.0 | 114840.0 | 2015
Lightsource BP | Walton | Solar | PV | No | Solar |  | 1.7863 | LV | England | South East | KT122EG |  | 511550.0 | 168450.0 | 2011
Lightsource BP | West Bradley | Solar | PV | No | Solar |  | 1.029 | LV | England | South West | EX168BJ |  | 289684.0 | 114161.0 | 2012
Lightsource BP | West Farm | Solar | PV | No | Solar |  | 7.63 | LV | Wales | Wales | SA724UN |  | 199608.0 | 203981.0 | 2013
Lightsource BP | Westwood | Solar | PV | No | Solar |  | 9.181 | LV | England | South East | CT125AS |  | 635063.0 | 166833.0 | 2014
Lightsource BP | Wheal Jane | Solar | PV | No | Solar |  | 1.42 | LV | England | South West |  |  | 177412.0 | 42176.0 | 2011
Lightsource BP | Wick Red Farm | Solar | PV | No | Solar |  | 4.9535 | LV | England | South West | BS240HD |  | 331399.0 | 154837.0 | 2016
Lightsource BP | Wilburton | Solar | PV | No | Solar |  | 4.99 | LV | England | Eastern | CB63PU |  | 547655.0 | 274082.0 | 2011
Lightsource BP | Wrockwardine | Solar | PV | No | Solar |  | 10.468 | LV | England | West Midlands | TF50BJ |  | 361262.0 | 311911.0 | 2015
LondonEnergy | Londonwaste Ltd | Bioenergy | Bioenergy | No | MSW |  | 58 | LV | England | London | N183AG |  | 535050.0 | 192550.0 | 1970
Marchwood Power | Marchwood Power | Fossil Fuel | CCGT | No | Natural Gas |  | 898 | HV | England | South East | SO404BD |  | 438274.0 | 108147.0 | 2009
Moray Offshore Windfarm (East) Ltd | Moray Offshore Windfarm East Limited | Wind | Offshore | No | Wind |  | 950 | HV | England | Scotland | AB439BR |  |  |  | 2021
Octopus Investments | Abbots Ripton | Solar | PV | No | Solar |  | 24.6672 | LV | England | Eastern | PE282LQ |  | 522746.0 | 277158.0 | 2014
Octopus Investments | Apse New Barn | Solar | PV | No | Solar |  | 3.0658 | LV | England | South East | PO377PS |  | 456363.0 | 82780.0 | 2013
Octopus Investments | Ash Row Farm | Solar | PV | No | Solar |  | 4.9979 | LV | England | Yorkshire and Humber | LS256JJ |  | 451649.0 | 433677.0 | 2015
Octopus Investments | Avenue Farm | Solar | PV | No | Solar |  | 7.6484 | LV | England | Eastern | NR147PJ |  | 628770.0 | 303787.0 | 2015
Octopus Investments | Averill Farm | Solar | PV | No | Solar |  | 4.9979 | LV | England | East Midlands | DE556HB |  | 441094.0 | 361390.0 | 2015
Octopus Investments | Barn Farm | Solar | PV | No | Solar |  | 4.692 | LV | England | Eastern | CO112UX |  | 615682.0 | 231393.0 | 2015
Octopus Investments | Bentley | Solar | PV | No | Solar |  | 5.0984 | LV | England | North West | CW13PL |  | 368446.0 | 356533.0 | 2013
Octopus Investments | Birch Estate | Solar | PV | No | Solar |  | 4.998 | LV | England | Eastern | CO20NU |  | 593323.0 | 219800.0 | 2015
Octopus Investments | Bishops Sutton | Solar | PV | No | Solar |  | 12 | LV | England | South East | SO240AA |  | 459558.0 | 131825.0 | 2014
Octopus Investments | Blaby | Solar | PV | No | Solar |  | 3.4802 | LV | England | East Midlands | LE85QW |  | 458722.0 | 296614.0 | 2016
Octopus Investments | Bradford | Solar | PV | No | Solar |  | 5.2874 | LV | England | South West | EX226LQ |  | 227973.0 | 100750.0 | 2013
Octopus Investments | Bratton Fleming | Solar | PV | No | Solar |  | 4.9921 | LV | England | South West | EX327LG |  | 265395.0 | 137979.0 | 2013
Octopus Investments | Brickkiln Lane | Solar | PV | No | Solar |  | 4.9933 | LV | England | Eastern | NR148AJ |  | 620403.0 | 299944.0 | 2016
Octopus Investments | Bryn Yr Odyn | Solar | PV | No | Solar |  | 14.8971 | LV | Wales | Wales | LL625DE |  | 239600.0 | 373400.0 | 2015
Octopus Investments | Burntstalk Farm | Solar | PV | No | Solar |  | 11.5248 | LV | England | Eastern | PE321JA |  | 577721.0 | 311630.0 | 2013
Octopus Investments | Bystock Farm | Solar | PV | No | Solar |  | 4.05 | LV | England | South West | EX85ED |  | 302289.0 | 84362.0 | 2015
Octopus Investments | Carlisle Estate | Solar | PV | No | Solar |  | 4.9979 | LV | England | North West | CA57ES |  | 336020.0 | 546015.0 | 2016
Octopus Investments | Caswell | Solar | PV | No | Solar |  | 5.9054 | LV | England | South West | BA229RH |  | 357538.0 | 109283.0 | 2016
Octopus Investments | Causilgey | Solar | PV | No | Solar |  | 4.998 | LV | England | South West | TR49EP |  | 177775.0 | 47586.0 | 2013
Octopus Investments | Chawton | Solar | PV | No | Solar |  | 3.6544 | LV | England | South East | PO318QT |  | 449357.0 | 93055.0 | 2013
Octopus Investments | Chediston Hall | Solar | PV | No | Solar |  | 12.348 | LV | England | Eastern | IP190RA |  | 636663.0 | 278367.0 | 2013
Octopus Investments | Chisbon | Solar | PV | No | Solar |  | 12.338 | LV | England | Eastern | CO168HJ |  | 612862.0 | 218208.0 | 2015
Octopus Investments | Chittering 2 | Solar | PV | No | Solar |  | 6.3046 | LV | England | Eastern | CB259PH |  | 551264.0 | 270881.0 | 2013
Octopus Investments | Clann Farm | Solar | PV | No | Solar |  | 1.489 | LV | England | South West | PL305HD |  | 202639.0 | 63931.0 | 2014
Octopus Investments | Cloford Common Farm | Solar | PV | No | Solar |  | 4.9993 | LV | England | South West | BA114PE |  | 373029.0 | 143593.0 | 2015
Octopus Investments | Corntown Solar | Solar | PV | No | Solar |  | 2.4832 | LV | Wales | Wales | CF355FB |  | 293545.0 | 177153.0 | 2017
Octopus Investments | Crapnell Farm | Solar | PV | No | Solar |  | 4.6679 | LV | England | South West | BA53HG |  | 359691.0 | 145698.0 | 2014
Octopus Investments | Craymarsh | Solar | PV | No | Solar |  | 1.8161 | LV | England | South West | SN126RG |  | 393506.0 | 162624.0 | 2012
Octopus Investments | Cressing | Solar | PV | No | Solar |  | 4.9939 | LV | England | Eastern | CM778PD |  | 579757.0 | 218798.0 | 2016
Octopus Investments | Dairy House Farm | Solar | PV | No | Solar |  | 3.366 | LV | England | North West | CW56DN |  | 365834.0 | 356455.0 | 2016
Octopus Investments | Decoy | Solar | PV | No | Solar |  | 5.3424 | LV | England | South East | PO203TR |  | 492213.0 | 104099.0 | 2014
Octopus Investments | Deepdale | Solar | PV | No | Solar |  | 4.9972 | LV | England | East Midlands | NG348SH |  | 507434.0 | 349013.0 | 2016
Octopus Investments | Drapers Farm | Solar | PV | No | Solar |  | 5.9986 | LV | England | Eastern | CM31QF |  | 572146.0 | 220468.0 | 2014
Octopus Investments | Eakring | Solar | PV | No | Solar |  | 11.7931 | LV | England | East Midlands | NG220AN |  | 466033.0 | 362403.0 | 2015
Octopus Investments | Ellicombe | Solar | PV | No | Solar |  | 1.3257 | LV | England | South West | EX175LS |  | 274429.0 | 105004.0 | 2013
Octopus Investments | Ermine Street | Solar | PV | No | Solar |  | 32.4494 | LV | England | East Midlands | NG348QT |  | 499291.0 | 347452.0 | 2014
Octopus Investments | Fullerton | Solar | PV | No | Solar |  | 4.3566 | LV | England | South East | SP117HR |  | 437054.0 | 141581.0 | 2017
Octopus Investments | Guisborough | Solar | PV | No | Solar |  | 4.9993 | LV | England | North East | TS146QX |  | 460407.0 | 516083.0 | 2016
Octopus Investments | Hatchlands | Solar | PV | No | Solar |  | 5.2175 | LV | England | South West | TQ97LB |  | 273302.0 | 59712.0 | 2013
Octopus Investments | Hazard | Solar | PV | No | Solar |  | 5.6566 | LV | England | South West | TQ97LN |  | 274991.0 | 59302.0 | 2014
Octopus Investments | Hewas | Solar | PV | No | Solar |  | 5.9829 | LV | England | South West | TR24EP |  | 191590.0 | 53161.0 | 2013
Octopus Investments | Higher Knapp Farm | Solar | PV | No | Solar |  | 1.5116 | LV | England | South West | TA36AY |  | 330222.0 | 124913.0 | 2013
Octopus Investments | Higher Trenhayle | Solar | PV | No | Solar |  | 2.9322 | LV | England | South West | TR275JU |  | 158256.0 | 36251.0 | 2013
Octopus Investments | Hill End Farm | Solar | PV | No | Solar |  | 2.84 | LV | England | South East | RG265HA |  | 462034.0 | 157344.0 | 2014
Octopus Investments | Hill Farm (OI) | Solar | PV | No | Solar |  | 10.8443 | LV | England | South East | PO360BB |  | 461387.0 | 89012.0 | 2014
Octopus Investments | Hollamoor | Solar | PV | No | Solar |  | 2.2363 | LV | England | South West | EX313HX |  | 254698.0 | 129964.0 | 2013
Octopus Investments | Holtwood | Solar | PV | No | Solar |  | 4.9941 | LV | England | East Midlands | DE65JW |  | 412619.0 | 333405.0 | 2016
Octopus Investments | Hullavington | Solar | PV | No | Solar |  | 8.316 | LV | England | South West | SN146QP |  | 389154.0 | 182299.0 | 2014
Octopus Investments | Lawn Lane | Solar | PV | No | Solar |  | 4.3235 | LV | England | West Midlands | WV95BB |  | 390095.0 | 304875.0 | 2016
Octopus Investments | Lenham | Solar | PV | No | Solar |  | 6.6067 | LV | England | South East | ME172HX |  | 589450.0 | 151072.0 | 2012
Octopus Investments | Lexham | Solar | PV | No | Solar |  | 7.9184 | LV | England | Eastern | PE322RY |  | 587463.0 | 319985.0 | 2013
Octopus Investments | Little Morton | Solar | PV | No | Solar |  | 14.289 | LV | England | East Midlands | DN228HE |  | 467187.0 | 379023.0 | 2014
Octopus Investments | Little T | Solar | PV | No | Solar |  | 5.4439 | LV | England | South West | TR109EF |  | 171916.0 | 31778.0 | 2013
Octopus Investments | Littleton Farm | Solar | PV | No | Solar |  | 12.0057 | LV | England | South West | DT119QP |  | 388332.0 | 105051.0 | 2015
Octopus Investments | Lochcraigs Farm | Solar | PV | No | Solar |  | 4.992 | LV | Scotland | Scotland | KA204LB |  | 227518.0 | 643857.0 | 2017
Octopus Investments | Lodge Farm | Solar | PV | No | Solar |  | 11.9975 | LV | England | East Midlands | NG139PL |  | 478519.0 | 341598.0 | 2014
Octopus Investments | Lovedean | Solar | PV | No | Solar |  | 4.5438 | LV | England | South East | PO80SH |  | 468005.0 | 112956.0 | 2013
Octopus Investments | Manor Farm Dorset | Solar | PV | No | Solar |  | 4.922 | LV | England | South West | SP85PR |  | 377815.0 | 128359.0 | 2014
Octopus Investments | Manston Thorne | Solar | PV | No | Solar |  | 6.1986 | LV | England | South East | CT125DS |  | 633388.0 | 164922.0 | 2014
Octopus Investments | Marley Thatch | Solar | PV | No | Solar |  | 6.2227 | LV | England | South West | TQ109LW |  | 271573.0 | 59890.0 | 2013
Octopus Investments | Meadow Farm | Solar | PV | No | Solar |  | 6.114 | LV | England | Eastern | IP264RG |  | 572611.0 | 296975.0 | 2014
Octopus Investments | Melbourn Black Peak | Solar | PV | No | Solar |  | 18.9552 | LV | England | Eastern | SG87ND |  | 540507.0 | 244190.0 | 2015
Octopus Investments | Melbourn Muncey Farm | Solar | PV | No | Solar |  | 30.9417 | LV | England | Eastern | SG86DG |  | 537951.0 | 242629.0 | 2015
Octopus Investments | Mill Hill Farm | Solar | PV | No | Solar |  | 4.9979 | LV | England | Yorkshire and Humber | YO606QN |  | 463388.0 | 467066.0 | 2015
Octopus Investments | Molland Farm | Solar | PV | No | Solar |  | 4.9985 | LV | England | South West | EX363PS |  | 282422.0 | 126165.0 | 2015
Octopus Investments | Mopley/Cadland | Solar | PV | No | Solar |  | 3.016 | LV | England | South East | SO451YH |  | 444681.0 | 100949.0 | 2013
Octopus Investments | Mount Mill | Solar | PV | No | Solar |  | 11.9998 | LV | England | East Midlands | MK196DG |  | 476366.0 | 237708.0 | 2015
Octopus Investments | Natewood | Solar | PV | No | Solar |  | 8.978 | LV | England | South East | BN273PH |  | 557796.0 | 107151.0 | 2015
Octopus Investments | New Row Farm | Solar | PV | No | Solar |  | 4.4504 | LV | England | South West | BA44JT |  | 363204.0 | 145130.0 | 2014
Octopus Investments | Newlands | Solar | PV | No | Solar |  | 4.279 | LV | England | South West | EX135SF |  | 333040.0 | 97434.0 | 2013
Octopus Investments | Ninnis | Solar | PV | No | Solar |  | 3.8822 | LV | England | South West | PL267EN |  | 198252.0 | 50490.0 | 2013
Octopus Investments | North Perrott Fruit Farm | Solar | PV | No | Solar |  | 0.8232 | LV | England | South West | TA187SN |  | 346475.0 | 110116.0 | 2013
Octopus Investments | North Wayton | Solar | PV | No | Solar |  | 8.3982 | LV | England | South West | PL126QQ |  | 242671.0 | 62588.0 | 2014
Octopus Investments | Northmoor | Solar | PV | No | Solar |  | 4.9149 | LV | England | South West | EX226TD |  | 227223.0 | 97462.0 | 2015
Octopus Investments | Oaklands | Solar | PV | No | Solar |  | 6.8544 | LV | England | South West | TN261ER |  | 596397.0 | 144740.0 | 2015
Octopus Investments | Ottringham | Solar | PV | No | Solar |  | 6.073 | LV | England | Yorkshire and Humber | HU120AD |  | 527561.0 | 424182.0 | 2014
Octopus Investments | Palfreys Barton | Solar | PV | No | Solar |  | 0.96138 | LV | England | South West | EX167RZ |  | 296533.0 | 118055.0 | 2013
Octopus Investments | Parciau | Solar | PV | No | Solar |  | 12.7195 | LV | Wales | Wales | LL551TS |  | 250255.0 | 365482.0 | 2015
Octopus Investments | Park Wall | Solar | PV | No | Solar |  | 4.998 | LV | England | South West | TA70HY |  | 332133.0 | 136030.0 | 2012
Octopus Investments | Parkhouse | Solar | PV | No | Solar |  | 6.6405 | LV | England | South East | SP97UZ |  | 422792.0 | 144085.0 | 2013
Octopus Investments | Penhale | Solar | PV | No | Solar |  | 3.5251 | LV | England | South West | PL277RQ |  | 194606.0 | 71371.0 | 2013
Octopus Investments | Penyrheollas | Solar | PV | No | Solar |  | 4.9862 | LV | Wales | Wales | NP120HY |  | 318604.0 | 201211.0 | 2017
Octopus Investments | Peter Hill | Solar | PV | No | Solar |  | 4.9979 | LV | England | Yorkshire and Humber | YO614PN |  | 450038.0 | 473183.0 | 2016
Octopus Investments | Peterlee | Solar | PV | No | Solar |  | 4.9972 | LV | England | North East | SR83UJ |  | 440912.0 | 542443.0 | 2016
Octopus Investments | Pingewood | Solar | PV | No | Solar |  | 15.3666 | LV | England | South East | RG303UG |  |  |  | 2015
Octopus Investments | Pitchford | Solar | PV | No | Solar |  | 21.0084 | LV | England | West Midlands |  |  | 350965.0 | 302668.0 | 2015
Octopus Investments | Pitts Farm | Solar | PV | No | Solar |  | 3.2141 | LV | England | South West | BA53HG |  | 359176.0 | 146235.0 | 2014
Octopus Investments | Pollington Airfield | Solar | PV | No | Solar |  | 4.9979 | LV | England | Yorkshire and Humber | DN140BA |  | 461763.0 | 420790.0 | 2015
Octopus Investments | Pyde Drove | Solar | PV | No | Solar |  | 8.436 | LV | England | South West | TA78DN |  | 335530.0 | 142499.0 | 2014
Octopus Investments | Ratcliffe House Farm | Solar | PV | No | Solar |  | 3.498 | LV | England | East Midlands | CV93LZ |  | 433432.0 | 299754.0 | 2015
Octopus Investments | Reaches Farm | Solar | PV | No | Solar |  | 6.2436 | LV | England | Eastern | IP265LA |  | 573913.0 | 298817.0 | 2014
Octopus Investments | Rew Farm | Solar | PV | No | Solar |  | 5.0627 | LV | England | South West | PL305AW |  | 209034.0 | 61130.0 | 2014
Octopus Investments | Rudge Manor | Solar | PV | No | Solar |  | 6.3872 | LV | England | South West | SN82HN |  | 427444.0 | 169114.0 | 2013
Octopus Investments | Rydon Farm | Solar | PV | No | Solar |  | 9.5763 | LV | England | South West | TQ126DB |  | 284136.0 | 68721.0 | 2015
Octopus Investments | Ryston Farm | Solar | PV | No | Solar |  | 4.6231 | LV | England | Eastern | PE380AA |  | 561681.0 | 302008.0 | 2015
Octopus Investments | Seaton Road | Solar | PV | No | Solar |  | 4.16 | LV | England | East Midlands | LE159BG |  | 487565.0 | 299395.0 | 2017
Octopus Investments | Shipton Bellinger | Solar | PV | No | Solar |  | 5.4331 | LV | England | South East | SP40EG |  | 423437.0 | 143998.0 | 2013
Octopus Investments | Short Hazel | Solar | PV | No | Solar |  | 4.9993 | LV | England | East Midlands | DE117BD |  | 433077.0 | 319883.0 | 2016
Octopus Investments | Singrug | Solar | PV | No | Solar |  | 11.9959 | LV | Wales | Wales | NP122BG |  | 319137.0 | 193566.0 | 2015
Octopus Investments | Six Hills | Solar | PV | No | Solar |  | 18.7387 | LV | England | East Midlands | LE143PR |  | 463321.0 | 321230.0 | 2015
Octopus Investments | Slaughtergate | Solar | PV | No | Solar |  | 1.8385 | LV | England | South West | SP85NH |  | 378233.0 | 127441.0 | 2013
Octopus Investments | Somerton Door | Solar | PV | No | Solar |  | 8.701 | LV | England | South West | TA116JA |  | 347045.0 | 130025.0 | 2015
Octopus Investments | Southcombe Farm | Solar | PV | No | Solar |  | 1.2127 | LV | England | South West | EX215RF |  | 244284.0 | 111956.0 | 2013
Octopus Investments | Spittleborough | Solar | PV | No | Solar |  | 9.1443 | LV | England | South West | SN48ET |  | 408318.0 | 183058.0 | 2014
Octopus Investments | Staining Wood | Solar | PV | No | Solar |  | 4.9979 | LV | England | North West | PR43PH |  | 336929.0 | 432551.0 | 2016
Octopus Investments | Stormy Down | Solar | PV | No | Solar |  | 4.672 | LV | Wales | Wales | CF334RS |  | 284154.0 | 180554.0 | 2017
Octopus Investments | Stratton Hall | Solar | PV | No | Solar |  | 11.7649 | LV | England | Eastern | IP100PL |  | 625674.0 | 239588.0 | 2014
Octopus Investments | Strete | Solar | PV | No | Solar |  | 4.8546 | LV | England | South West | EX52PL |  | 304235.0 | 94913.0 | 2013
Octopus Investments | Sutton Mawr | Solar | PV | No | Solar |  | 7.524 | LV | Wales | Wales | CF623AB |  | 307224.0 | 170024.0 | 2014
Octopus Investments | Sycamore | Solar | PV | No | Solar |  | 19.0121 | LV | England | South East | TN299SY |  | 601943.0 | 125385.0 | 2014
Octopus Investments | Tavells | Solar | PV | No | Solar |  | 5.4106 | LV | England | South East | SO404WH |  | 438181.0 | 110655.0 | 2013
Octopus Investments | The Breck | Solar | PV | No | Solar |  | 4.9993 | LV | England | East Midlands | S432NP |  | 442323.0 | 376116.0 | 2016
Octopus Investments | The Hollies | Solar | PV | No | Solar |  | 8.605 | LV | England | East Midlands | PE244SH |  | 549558.0 | 363539.0 | 2013
Octopus Investments | The Hydes | Solar | PV | No | Solar |  | 10.7161 | LV | England | Eastern | CM74TX |  | 564210.0 | 230560.0 | 2014
Octopus Investments | Thoresby | Solar | PV | No | Solar |  | 19.8092 | LV | England | East Midlands | NG229EX |  | 460364.0 | 370225.0 | 2015
Octopus Investments | Tillhouse | Solar | PV | No | Solar |  | 10.5105 | LV | England | South West | EX53BG |  | 301013.0 | 96534.0 | 2014
Octopus Investments | Tooley Farm | Solar | PV | No | Solar |  | 4.9985 | LV | England | Eastern | CM63AA |  | 564888.0 | 223424.0 | 2015
Octopus Investments | Tredown Farm | Solar | PV | No | Solar |  | 1.4348 | LV | England | South West | PL160HH |  | 239431.0 | 81407.0 | 2013
Octopus Investments | Tregassow | Solar | PV | No | Solar |  | 5.8714 | LV | England | South West | TR49BL |  | 185395.0 | 49565.0 | 2013
Octopus Investments | Trench Farm | Solar | PV | No | Solar |  | 4.997 | LV | Wales | Wales | LL130NA |  | 338419.0 | 339068.0 | 2015
Octopus Investments | Turves | Solar | PV | No | Solar |  | 4.998 | LV | England | Eastern | PE72HS |  | 533992.0 | 294321.0 | 2013
Octopus Investments | Upper Farringdon | Solar | PV | No | Solar |  | 6.1758 | LV | England | South East | GU343HW |  | 471468.0 | 135482.0 | 2015
Octopus Investments | Walland Farm | Solar | PV | No | Solar |  | 4.9993 | LV | England | South West | EX395DP |  | 235344.0 | 122223.0 | 2015
Octopus Investments | Waterloo Farm 1 and 2 | Solar | PV | No | Solar |  | 28.6681 | LV | England | Eastern | SG192JW |  | 518826.0 | 251804.0 | 2015
Octopus Investments | Wedgehill | Solar | PV | No | Solar |  | 13.5078 | LV | England | South West | BH216SB |  | 406557.0 | 108809.0 | 2015
Octopus Investments | Week Farm 2 | Solar | PV | No | Solar |  | 3.7301 | LV | England | South West | EX387HU |  | 251218.0 | 119059.0 | 2014
Octopus Investments | West Hall | Solar | PV | No | Solar |  | 5.511 | LV | Wales | Wales | CF624ZW |  | 302476.0 | 166946.0 | 2014
Octopus Investments | Westerfield | Solar | PV | No | Solar |  | 12.9793 | LV | England | South East | OX183PA |  | 427125.0 | 209714.0 | 2015
Octopus Investments | Westwood Farm | Solar | PV | No | Solar |  | 5.1469 | LV | England | East Midlands | NG220PF |  | 471765.0 | 370062.0 | 2014
Octopus Investments | Whiddon Farm | Solar | PV | No | Solar |  | 0.89739 | LV | England | South West | EX226PJ |  | 239451.0 | 97227.0 | 2013
Octopus Investments | Wiggin Hill | Solar | PV | No | Solar |  | 11.4436 | LV | England | Eastern | PE273LL |  | 530442.0 | 273663.0 | 2015
Octopus Investments | Willburton 2 (Mingay Farm) | Solar | PV | No | Solar |  | 19.3208 | LV | England | Eastern | CB63PU |  | 547073.0 | 272967.0 | 2014
Octopus Investments | Willsland | Solar | PV | No | Solar |  | 3.267 | LV | England | South West | EX215LS |  | 250049.0 | 104054.0 | 2013
Octopus Investments | Woodlands Farm | Solar | PV | No | Solar |  | 13.1592 | LV | England | South East | CT34NB |  | 617569.0 | 163068.0 | 2015
Orsted | Barrow | Wind | Offshore | No | Wind |  | 90 | HV | England | North West |  |  | 314978.0 | 455827.0 | 2006
Orsted | Burbo | Wind | Offshore | No | Wind |  | 90 | LV | England | North West |  |  | 321476.0 | 399706.0 | 2008
Orsted | Burbo Extension | Wind | Offshore | No | Wind |  | 259 | HV | England | North West |  |  | 315815.0 | 398892.0 | 2016
Orsted | Gunfleet Sands 01 | Wind | Offshore | No | Wind |  | 108 | HV | England | South East |  |  | 622317 | 208468 | 2010
Orsted | Gunfleet Sands 02 | Wind | Offshore | No | Wind |  | 67 | HV | England | South East |  |  | 622317 | 622317 | 2010
Orsted | Gunfleet Sands Demo | Wind | Offshore | No | Wind |  | 12 | HV | England | South East |  |  | 620650.0 | 205297.0 | 2013
Orsted | Hornsea 01 | Wind | Offshore | No | Wind |  | 1218 | HV | England | North East |  |  | 626000.0 | 426000.0 | 2019
Orsted | Hornsea 02 Soundmark | Wind | Offshore | No | Wind |  | 1386 | HV | England | North East |  |  | 626000.0 | 426000.0 | 2022
Orsted | Lincs | Wind | Offshore | No | Wind |  | 270 | HV | England | East Midlands |  |  | 567020.0 | 368144.0 | 2013
Orsted | Race Bank | Wind | Offshore | No | Wind |  | 573 | HV | England | Eastern |  |  | 573300.0 | 363000.0 | 2018
Orsted | Walney 01 | Wind | Offshore | No | Wind |  | 183 | HV | England | North West |  |  | 300833 | 461449 | 2011
Orsted | Walney 02 | Wind | Offshore | No | Wind |  | 183 | HV | England | North West |  |  | 300833 | 461449 | 2012
Orsted | Walney 03 | Wind | Offshore | No | Wind |  | 330 | HV | England | North West |  |  | 295033.0 | 466313.0 | 2017
Orsted | Walney 04 | Wind | Offshore | No | Wind |  | 329 | HV | England | North West |  |  | 320039.0 | 464000.0 | 2018
Orsted | West of Duddon Sands | Wind | Offshore | No | Wind |  | 389 | HV | England | North West |  |  | 304230.0 | 455334.0 | 2014
Orsted | Westermost Rough | Wind | Offshore | No | Wind |  | 210 | HV | England | Yorkshire and Humber |  |  | 541677.0 | 436555.0 | 2015
Part of Drax Group | Bonnington | Hydro | Natural Flow | No | Hydro |  | 11 | LV | Scotland | Scotland | ML119TB |  | 288851.29212100001 | 641742.81936800003 | 1927
Part of Drax Group | Carsfad | Hydro | Natural Flow | No | Hydro |  | 12 | LV | Scotland | Scotland | DG73ST |  | 259672.544711 | 584952.22294799995 | 1935
Part of Drax Group | Drax Power Station Biomass Units | Bioenergy | Bioenergy | No | Biomass |  | 2640 | HV | England | Yorkshire and Humber | YO88PH |  | 466650.0 | 427050.0 | 2013
Part of Drax Group | Drumjohn | Hydro | Natural Flow | No | Hydro |  | 1 | LV | Scotland | Scotland | DG73TJ |  | 252514.43564800001 | 597670.45692799997 | 1935
Part of Drax Group | Earlstoun | Hydro | Natural Flow | No | Hydro |  | 14 | LV | Scotland | Scotland | DG73SR |  | 261304.67353900001 | 583126.64510099997 | 1935
Part of Drax Group | Glenlee | Hydro | Natural Flow | No | Hydro |  | 24 | LV | Scotland | Scotland | DG73SF |  | 261221.35846700001 | 580243.46073699999 | 1935
Part of Drax Group | Kendoon | Hydro | Natural Flow | No | Hydro |  | 24 | LV | Scotland | Scotland | DG73UB |  | 261359.07337200001 | 589083.399385 | 1935
Part of Drax Group | Stonebyres | Hydro | Natural Flow | No | Hydro |  | 6 | LV | Scotland | Scotland | ML119UP |  | 284977.43216500001 | 644040.90092599997 | 1927
Part of Drax Group | Tongland | Hydro | Natural Flow | No | Hydro |  | 33 | LV | Scotland | Scotland | DG64LT |  | 270138.10144599999 | 554580.98591599998 | 1935
Part of PX Group | Fellside CHP | Fossil Fuel | CCGT | Yes | Natural Gas |  | 105 | HV | England | North West | CA201PG |  | 303202.0 | 503793.0 | 1995
Pennant Walters | Maesgwyn | Wind | Onshore | No | Wind |  | 26 | HV | Wales | Wales |  | SASN86400890 | 285500.0 | 205500.0 | 2011
Pennant Walters | Maesgwyn Extension | Wind | Onshore | No | Wind |  | 2.5 | HV | Wales | Wales |  | SN8710908818 | 286568.0 | 205930.0 | 2017
Pennant Walters | Maesgwyn Solar | Solar | PV | No | Solar |  | 2.5 | LV | Wales | Wales |  | SASN86400890 | 288678.0 | 207067.0 | 2017
Pennant Walters | Mynydd Bwllfa | Wind | Onshore | No | Wind |  | 22.5 | HV | Wales | Wales | CF449NB |  | 295979.0 | 205172.0 | 2015
Pennant Walters | Pant y Wal | Wind | Onshore | No | Wind |  | 52.5 | HV | Wales | Wales | CF356ED |  | 295886.0 | 191521.0 | 2013
Pennant Walters | Pant y Wal Extension | Wind | Onshore | No | Wind |  | 20 | HV | Wales | Wales | CF356ED |  | 294649.0 | 188695.0 | 2017
Quintas Energy | Astley | Solar | PV | No | Solar |  | 4.992 | LV | England | West Midlands | WV156ER |  | 378234.0 | 286133.0 | 2016
Quintas Energy | Chalcroft | Solar | PV | No | Solar |  | 6.3396 | LV | England | South East | SO302HU |  | 448713.0 | 116890.0 | 2013
Quintas Energy | Pen y cae | Solar | PV | No | Solar |  | 4.9694 | LV | Wales | Wales | LL141TP |  | 328970.0 | 344020.0 | 2016
Quintas Energy | Willersey | Solar | PV | No | Solar |  | 3.7814 | LV | England | South West | WR117HF |  | 409850.0 | 240750.0 | 2014
RES Group | Altahullion Extension Wind Farm (NI) | Wind | Onshore | No | Wind |  | 11.7 | LV | Northern Ireland | Northern Ireland | BT474NS |  | 78039.0 | 574408.0 | 2007
RES Group | Altahullion Wind Farm (NI) | Wind | Onshore | No | Wind |  | 26 | LV | Northern Ireland | Northern Ireland | BT474NS |  | 78039.0 | 574408.0 | 2003
RES Group | Auquhirie Land | Wind | Onshore | No | Wind |  | 6.9 | HV | Scotland | Scotland | AB393XB |  | 328500.0 | 785500.0 | 2013
RES Group | Barlborough | Wind | Onshore | No | Wind |  | 0.85 | LV | England | East Midlands |  |  | 448975.0 | 376975.0 | 2015
RES Group | Batsworthy Cross | Wind | Onshore | No | Wind |  | 10 | LV | England | South West |  |  | 282928.0 | 121610.0 | 2016
RES Group | Beinneun Wind Farm | Wind | Onshore | No | Wind |  | 108.8 | HV | Scotland | Scotland | IV637YV |  |  |  | 2017
RES Group | Bilsthorpe | Wind | Onshore | No | Wind |  | 10.25 | LV | England | East Midlands |  |  | 466000.0 | 362000.0 | 2013
RES Group | Black Hill Wind Farm | Wind | Onshore | No | Wind |  | 28.6 | LV | Scotland | Scotland |  | NT730555 | 373000.0 | 656300.0 | 2007
RES Group | Blary Hill | Wind | Onshore | No | Wind |  | 35 | HV | England | Scotland | PA296UZ |  |  |  | 2022
RES Group | Brackagh Quarry | Wind | Onshore | No | Wind |  | 5.001 | LV | Northern Ireland | Northern Ireland |  |  | 97617.0 | 556429.0 | 2016
RES Group | Braich Ddu | Wind | Onshore | No | Wind |  | 3.9 | LV | Wales | Wales |  |  | 267500.0 | 301500.0 | 2007
RES Group | Burnthouse Windfarm | Wind | Onshore | No | Wind |  | 6 | LV | England | Eastern |  |  | 533458.0 | 295082.0 | 2013
RES Group | Burton Wold | Wind | Onshore | No | Wind |  | 14.4 | HV | England | East Midlands |  |  | 491902.0 | 274577.0 | 2014
RES Group | Burton Wold South (GB) | Wind | Onshore | No | Wind |  | 8.25 | HV | England | East Midlands |  |  |  |  | 2017
RES Group | Carscreugh | Wind | Onshore | No | Wind |  | 15.3 | HV | Scotland | Scotland |  |  | 225000.0 | 555000.0 | 2014
RES Group | Castle Craig | Wind | Onshore | No | Wind |  | 25 | LV | Northern Ireland | Northern Ireland | BT817SN |  | 39597.0 | 540549.0 | 2018
RES Group | Castle Pill Farm 1 - A, C | Wind | Onshore | No | Wind |  | 3.148 | HV | Wales | Wales |  |  | 192398.0 | 207108.0 | 2004
RES Group | Chalgrove Solar Limited | Solar | PV | No | Solar |  | 21.34 | LV | England | South East |  | SU649967 | 465126.0 | 197272.0 | 2015
RES Group | Cour Wind Farm | Wind | Onshore | No | Wind |  | 20.5 | HV | Scotland | Scotland | PA286QL |  | 181005.0 | 648528.0 | 2017
RES Group | Den Brook Wind Farm (GB) | Wind | Onshore | No | Wind |  | 18 | LV | England | South West | EX202BJ |  | 268496.0 | 101120.0 | 2016
RES Group | Denzell Downs Windfarm | Wind | Onshore | No | Wind |  | 10 | LV | England | South West |  |  | 189923.0 | 67094.0 | 2015
RES Group | Derriton (Tamar Heights) | Solar | PV | No | Solar |  | 11.7 | LV | England | South West | EX226JX |  | 233249.0 | 103010.0 | 2014
RES Group | Dungavel | Wind | Onshore | No | Wind |  | 26 | HV | Scotland | Scotland |  |  | 267954.0 | 636995.0 | 2015
RES Group | Dyffryn Brodyn Wind Farm (GB) | Wind | Onshore | No | Wind |  | 5.4 | LV | Wales | Wales | SA340JE |  | 222100.0 | 226800.0 | 1994
RES Group | Earlseat Wind Farm (GB) | Wind | Onshore | No | Wind |  | 16 | LV | Scotland | Scotland | HY14TQ |  | 332961.0 | 698416.0 | 2013
RES Group | Egmere | Solar | PV | No | Solar |  | 21 | LV | England | Eastern | NR226AY |  | 590428.0 | 338001.0 | 2014
RES Group | Ferndale Wind Farm | Wind | Onshore | No | Wind |  | 6.4 | HV | Wales | Wales |  |  | 299700.0 | 195700.0 | 2011
RES Group | Forss Extension Wind Farm (GB) | Wind | Onshore | No | Wind |  | 5.2 | LV | Scotland | Scotland | KW147U |  | 302000.0 | 969500.0 | 2007
RES Group | Forss Wind Farm (GB) | Wind | Onshore | No | Wind |  | 2 | LV | Scotland | Scotland | KW147U |  | 302000.0 | 969500.0 | 2003
RES Group | Four Burrows Solar (Kenwyn) | Solar | PV | No | Solar |  | 7.2 | LV | England | South West | TR48JB |  | 176372.0 | 48050.0 | 2015
RES Group | Four Burrows Wind Farm (GB) | Wind | Onshore | No | Wind |  | 4.5 | LV | England | South West | TR48JB |  | 176000.0 | 48200.0 | 1995
RES Group | Freasdail (GB) | Wind | Onshore | No | Wind |  | 22.5 | HV | Scotland | Scotland | PA296XR |  | 180721.0 | 660754.0 | 2017
RES Group | French Farm Wind Farm | Wind | Onshore | No | Wind |  | 4 | LV | England | Eastern |  |  | 528300.0 | 309000.0 | 2016
RES Group | Garreg Llwyd (GB) | Wind | Onshore | No | Wind |  | 30.4 | LV | Wales | Wales | LD16YS |  | 294491.0 | 272407.0 | 2017
RES Group | Glenchamber Wind Farm (GB) | Wind | Onshore | No | Wind |  | 25.3 | LV | Scotland | Scotland | DG80PB |  | 224474.0 | 564039.0 | 2016
RES Group | Glens of Foudland | Wind | Onshore | No | Wind |  | 26 | LV | Scotland | Scotland |  |  | 361496.0 | 837303.0 | 2009
RES Group | Goonhilly Downs Wind Farm | Wind | Onshore | No | Wind |  | 12 | LV | England | South West |  |  | 171000.0 | 21200.0 | 2008
RES Group | Goonhilly Solar | Solar | PV | No | Solar |  | 4.51 | LV | England | South West |  |  | 169711.0 | 21226.0 | 2014
RES Group | Grange Wind Farm | Wind | Onshore | No | Wind |  | 12.3 | LV | England | Yorkshire and Humber | DN158RY |  | 486042.0 | 416496.0 | 2016
RES Group | Grange Wind Farm (GB) | Wind | Onshore | No | Wind |  | 14 | LV | England | East Midlands | PE135RB |  | 545055.0 | 318754.0 | 2013
RES Group | Hale Farm Solar Ltd | Solar | PV | No | Solar |  | 12.23 | LV | England | South West |  |  | 419461.0 | 137939.0 | 2015
RES Group | Hall Farm Wind Farm | Wind | Onshore | No | Wind |  | 24.6 | HV | England | Yorkshire and Humber |  |  | 507865.0 | 443185.0 | 2013
RES Group | Hallburn Farm Wind Farm | Wind | Onshore | No | Wind |  | 13.2 | LV | England | North west |  |  |  |  | 2018
RES Group | High Down | Wind | Onshore | No | Wind |  | 0.5 | LV | England | South West |  |  | 230770.0 | 69217.0 | 2014
RES Group | High Haswell Wind Farm | Wind | Onshore | No | Wind |  | 4 | LV | England | North East |  |  | 436675.0 | 543772.0 | 2011
RES Group | High Pow | Wind | Onshore | No | Wind |  | 3.9 | LV | England | North West |  |  | 323550.0 | 544400.0 | 2015
RES Group | High Sharpley | Wind | Onshore | No | Wind |  | 2.6 | LV | England | North East |  |  | 442644.0 | 549702.0 | 2006
RES Group | Hill of Towie Wind Farm (GB) | Wind | Onshore | No | Wind |  | 48.3 | LV | Scotland | Scotland | AB556YU |  | 320000.0 | 860000.0 | 2012
RES Group | Jacks Lane (GB) | Wind | Onshore | No | Wind |  | 15 | LV | England | Eastern | PE318PZ |  | 580388.0 | 335874.0 | 2015
RES Group | Kelburn Wind Farm (GB) | Wind | Onshore | No | Wind |  | 28 | LV | Scotland | Scotland | KA245LE |  | 224000.0 | 655000.0 | 2012
RES Group | Lendrums Bridge Extension Wind Farm (NI) | Wind | Onshore | No | Wind |  | 7.3 | LV | Northern Ireland | Northern Ireland | BT750LL |  | 54170.0 | 517391.0 | 2002
RES Group | Lendrums Bridge Wind Farm (NI) | Wind | Onshore | No | Wind |  | 5.94 | LV | Northern Ireland | Northern Ireland | BT750LL |  | 63672.0 | 512074.0 | 2000
RES Group | Little Raith (GB) | Wind | Onshore | No | Wind |  | 24.8 | LV | Scotland | Scotland | KY50AX |  |  |  | 2020
RES Group | Llynfi Afan Renewable Energy Limited | Wind | Onshore | No | Wind |  | 24 | HV | Wales | Wales |  |  | 289252.0 | 196198.0 | 2017
RES Group | Loscar | Wind | Onshore | No | Wind |  | 4.5 | LV | England | Yorkshire and Humber |  |  | 451000.0 | 380000.0 | 2010
RES Group | Lough Hill Wind Farm (NI) | Wind | Onshore | No | Wind |  | 7.8 | LV | Northern Ireland | Northern Ireland | BT817SL |  | 38467.0 | 541020.0 | 2007
RES Group | Marvel (Stone Farm) | Solar | PV | No | Solar |  | 5 | LV | England | South East | PO303BQ |  | 451260.0 | 86014.0 | 2015
RES Group | Meikle Carewe Wind Farm (GB) | Wind | Onshore | No | Wind |  | 10.2 | LV | Scotland | Scotland | AB393QH |  | 383200.0 | 792000.0 | 2013
RES Group | Mendennick Solar | Solar | PV | No | Solar |  | 2.64 | LV | England | South West |  |  | 241551.0 | 53320.0 | 2015
RES Group | Minnygap (GB) | Wind | Onshore | No | Wind |  | 25 | HV | Scotland | Scotland | DG109PX |  | 307313.0 | 597397.0 | 2017
RES Group | Muirhall South (GB) | Wind | Onshore | No | Wind |  | 8.25 | HV | Scotland | [5 empty] | 2016
RES Group | Mynydd Brombil | Wind | Onshore | No | Wind |  | 8 | LV | Wales | Wales |  |  | 279141.0 | 188569.0 | 2017
RES Group | Mynydd Portref | Wind | Onshore | No | Wind |  | 12 | LV | Wales | Wales |  |  | 298897.0 | 185178.0 | 2017
RES Group | Neilston (GB) | Wind | Onshore | No | Wind |  | 10 | LV | Scotland | Scotland | G784BZ |  | 245292.0 | 653952.0 | 2018
RES Group | New Albion | Wind | Onshore | No | Wind |  | 14.35 | HV | England | East Midlands |  |  | 483679.0 | 283792.0 | 2015
RES Group | Newton Ferrers | Solar | PV | No | Solar |  | 19.5 | LV | England | South West |  | SX359665 | 235294.0 | 67022.0 | 2015
RES Group | Orchard End Windfarm | Wind | Onshore | No | Wind |  | 4 | LV | England | North West |  |  | 343216.0 | 445233.0 | 2013
RES Group | Parley | Solar | PV | No | Solar |  | 24.2 | LV | England | South West | BH236BG |  | 409877.0 | 99146.0 | 2014
RES Group | Parsonage (Hazel) | Solar | PV | No | Solar |  | 7 | LV | England | South West | TA199EF |  | 336700.0 | 115500.0 | 2013
RES Group | Pen Bryn Oer Wind Farm | Wind | Onshore | No | Wind |  | 6 | LV | Wales | Wales |  |  | 312065.0 | 209235.0 | 2017
RES Group | Penare | Solar | PV | No | Solar |  | 11.1 | LV | England | South West | TR49DG |  | 181089.0 | 49385.0 | 2014
RES Group | Pencoose | Solar | PV | No | Solar |  | 8.14 | LV | England | South West |  | SW728379 | 173927.0 | 37998.0 | 2015
RES Group | Ramsey | Wind | Onshore | No | Wind |  | 1.8 | LV | England | Eastern |  |  | 528800.0 | 284900.0 | 2008
RES Group | Ramsey 2 Wind Farm | Wind | Onshore | No | Wind |  | 8 | LV | England | Eastern |  |  | 527814.0 | 286445.0 | 2013
RES Group | Rodbaston | Wind | Onshore | No | Wind |  | 4 | LV | England | West Midlands |  |  |  |  | 2016
RES Group | Roos Wind Farm (GB) | Wind | Onshore | No | Wind |  | 17.1 | LV | England | Yorkshire and Humber | HU120LA |  | 527376.0 | 430105.0 | 2013
RES Group | Roskrow Barton | Wind | Onshore | No | Wind |  | 1.7 | LV | England | South West |  |  | 176500.0 | 35500.0 | 2008
RES Group | Sancton Hill Wind Farm | Wind | Onshore | No | Wind |  | 10 | LV | England | Yorkshire and Humber |  |  | 491554.0 | 439660.0 | 2011
RES Group | Solwaybank | Wind | Onshore | No | Wind |  | 30.4 | HV | Scotland | [5 empty] | 2020
RES Group | South Sharpley Wind Farm | Wind | Onshore | No | Wind |  | 6 | LV | England | North East |  |  | 438490.0 | 549675.0 | 2011
RES Group | SPD 2 - Hall Farm | Solar | PV | No | Solar |  | 14.9 | LV | England | Eastern |  | TM195952 | 0.0 | 0.0 | 2015
RES Group | SPD 3 - Grange Farm | Solar | PV | No | Solar |  | 9.5 | LV | England | East Midlands |  | TF231620 | 523131.0 | 362337.0 | 2015
RES Group | SPD 4 - Gelliwern | Solar | PV | No | Solar |  | 6.24 | LV | Wales | Wales |  | SN626019 | 262382.0 | 202019.0 | 2015
RES Group | St Breock | Wind | Onshore | No | Wind |  | 10 | LV | England | South West |  |  | 198592.0 | 68218.0 | 2015
RES Group | Tallentire Wind Farm (GB) | Wind | Onshore | No | Wind |  | 12 | LV | England | North West | CA130QA |  | 312500.0 | 535500.0 | 2013
RES Group | Tormywheel | Wind | Onshore | No | Wind |  | 30.75 | LV | Scotland | Scotland |  |  | 294905.0 | 655232.0 | 2017
RES Group | Turncole Wind Farm (GB) | Wind | Onshore | No | Wind |  | 17.5 | LV | England | Eastern | CM08NE |  | 598484.0 | 196719.0 | 2017
RES Group | UK Solar (Hartwell) LLP | Solar | PV | No | Solar |  | 18.6 | LV | England | East Midlands |  | SP791490 | 478515.0 | 248927.0 | 2015
RES Group | UK Solar (Lower Newton) LLP | Solar | PV | No | Solar |  | 11.92 | LV | England | West Midlands |  | SJ988386 | 398731.0 | 338883.0 | 2014
RES Group | Wear Point Wind Farm | Wind | Onshore | No | Wind |  | 8.2 | HV | Wales | Wales |  |  | 193041.0 | 204629.0 | 2014
RES Group | Whittlesey | Wind | Onshore | No | Wind |  | 1.8 | LV | England | Eastern |  |  | 524027.0 | 297139.0 | 2015
RES Group | Wix Lodge (Stour Fields) | Solar | PV | No | Solar |  | 18.7 | LV | England | Eastern | CO112RP |  | 614962.0 | 228422.0 | 2014
RES Group | Woolley Hill (GB) | Wind | Onshore | No | Wind |  | 10 | LV | England | Eastern | PE280UA |  | 515374.0 | 272655.0 | 2015
RES Group | Wryde Croft Wind Farm (GB) | Wind | Onshore | No | Wind |  | 26 | LV | England | Eastern | PE60TP |  | 532606.0 | 307038.0 | 2016
River Nene | Peterborough Power Station | Fossil Fuel | Single cycle | No | Natural Gas |  | 245 | HV | England | Eastern | PE15NT |  | 518401.0 | 299217.0 | 1993
Riverside Resource Recovery | Riverside - Energy from Waste | Bioenergy | Bioenergy | No | MSW |  | 80 | HV | England | London | DA176JY |  | 547200.0 | 176500.0 | 2011
RWE Npower | An Suidhe | Wind | Onshore | No | Wind |  | 19.3 | HV | Scotland | Scotland |  |  | 200483.0 | 707563.0 | 2005
RWE Npower | Auchtertyre | Hydro | Natural Flow | No | Hydro |  | 0.6 | LV | Scotland | Scotland |  |  | 235422.0 | 729327.0 | 2000
RWE Npower | Bad a Cheo | Wind | Onshore | No | Wind |  | 26.65 | HV | Scotland | Scotland |  |  | 316615.0 | 948900.0 | 2018
RWE Npower | Bilbster | Wind | Onshore | No | Wind |  | 3.9 | LV | Scotland | Scotland |  |  | 327150.0 | 951850.0 | 2007
RWE Npower | Black Rock | Hydro | Natural Flow | No | Hydro |  | 3.5 | LV | Scotland | Scotland |  |  | 259900.0 | 866800.0 | 2012
RWE Npower | Bowbeat (Emly Bank) - RO | Wind | Onshore | No | Wind |  | 15.6 | LV | Scotland | Scotland |  |  | 329600.0 | 647500.0 | 2002
RWE Npower | Bowbeat (Roughside) - RO | Wind | Onshore | No | Wind |  | 15.6 | LV | Scotland | Scotland |  |  | 333000.0 | 646200.0 | 2002
RWE Npower | Bradwell | Wind | Onshore | No | Wind |  | 20.5 | LV | England | Eastern |  |  | 595000.0 | 205000.0 | 2013
RWE Npower | Braevallich | Hydro | Natural Flow | No | Hydro |  | 2.274 | LV | Scotland | Scotland |  |  | 196657.00008 | 706908.99997 | 2005
RWE Npower | Brechfa Forest West | Wind | Onshore | No | Wind |  | 57.4 | HV | Wales | Wales |  |  | 251493.0 | 233864.0 | 2018
RWE Npower | Burgar Hill | Wind | Onshore | No | Wind |  | 5 | LV | Scotland | Scotland |  |  | 334300.0 | 1026200.0 | 2006
RWE Npower | Butterwick Moor Circuit 1 | Wind | Onshore | No | Wind |  | 9.4 | LV | England | North East |  |  | 439000.0 | 530000.0 | 2011
RWE Npower | Butterwick Moor Circuit 2 | Wind | Onshore | No | Wind |  | 9.4 | LV | England | North East |  |  | 439000.0 | 530000.0 | 2011
RWE Npower | Camster | Wind | Onshore | No | Wind |  | 50 | LV | Scotland | Scotland |  |  | 325800.0 | 947400.0 | 2013
RWE Npower | Carnoch | Hydro | Natural Flow | No | Hydro |  | 1.35 | LV | Scotland | Scotland |  |  | 174589.83968400001 | 759870.61419600004 | 2009
RWE Npower | Cheshire | Fossil Fuel | Single cycle | No | Natural Gas |  | 90 | LV | England | North West | CH651AF |  |  |  | 2000
RWE Npower | Cia Aig | Hydro | Natural Flow | No | Hydro |  | 3 | LV | Scotland | Scotland |  |  | 217196.0 | 788748.0 | 2016
RWE Npower | Clocaenog Forest | Wind | Onshore | No | Wind |  | 96 | HV | Wales | Wales |  |  | 301568.0 | 359344.0 | 2019
RWE Npower | Cowes | Fossil Fuel | Single cycle | No | Diesel/Gas Oil |  | 140 | LV | England | South East | PO326JF |  | 448472.0 | 93554.0 | 1982
RWE Npower | Croesor | Hydro | Natural Flow | No | Hydro |  | 0.505 | LV | Wales | Wales |  |  | 264900.0 | 346000.0 | 1999
RWE Npower | Cwm Dyli | Hydro | Natural Flow | No | Hydro |  | 9.9 | LV | Wales | Wales |  |  | 257976.51233200001 | 360502.84342500003 | 2002
RWE Npower | Deucheran Hill (RO) | Wind | Onshore | No | Wind |  | 15.8 | LV | Scotland | Scotland |  |  | 177000.0 | 643000.0 | 2001
RWE Npower | Didcot B | Fossil Fuel | CCGT | No | Natural Gas |  | 1450 | HV | England | South East | OX117YU |  | 451077.0 | 182210.0 | 1998
RWE Npower | Didcot GT | Fossil Fuel | Single cycle | No | Diesel/Gas Oil |  | 100 | HV | England | South East | OX117YU |  | 451077.0 | 182210.0 | 1972
RWE Npower | Douglas Water | Hydro | Natural Flow | No | Hydro |  | 2.969 | LV | Scotland | Scotland |  |  | 204559.00006600001 | 706949.99997700006 | 2008
RWE Npower | Dulyn | Hydro | Natural Flow | No | Hydro |  | 0.505 | LV | Wales | Wales |  |  | 277754.0 | 368358.0 | 1998
RWE Npower | Galloper | Wind | Offshore | No | Wind |  | 352.8 | HV | England | Eastern |  | TM7796929898 | 646316.0 | 262379.0 | 2017
RWE Npower | Garnedd | Hydro | Natural Flow | No | Hydro |  | 0.56 | LV | Wales | Wales |  |  | 269641.31455499999 | 353035.80387900001 | 1990
RWE Npower | Garrogie | Hydro | Natural Flow | No | Hydro |  | 2.4 | LV | Scotland | Scotland |  |  | 250100.0 | 813300.0 | 2005
RWE Npower | Garry Gualach | Hydro | Natural Flow | No | Hydro |  | 0.78 | LV | Scotland | Scotland |  |  | 216600.0 | 799800.0 | 2002
RWE Npower | Glen Noe | Hydro | Natural Flow | No | Hydro |  | 2 | LV | Scotland | Scotland |  |  |  |  | 2021
RWE Npower | Glen Tarbert | Hydro | Natural Flow | No | Hydro |  | 0.85 | LV | Scotland | Scotland |  |  | 186600.0 | 760500.0 | 2000
RWE Npower | Goole Fields A | Wind | Onshore | No | Wind |  | 33 | HV | England | Yorkshire and Humber |  |  | 473487.0 | 419400.0 | 2013
RWE Npower | Goole Fields B | Wind | Onshore | No | Wind |  | 34.85 | HV | England | Yorkshire and Humber |  |  | 473632.0 | 420610.0 | 2016
RWE Npower | Great Eppleton (ex NFFO) | Wind | Onshore | No | Wind |  | 4.1 | LV | England | North East |  |  | 436900.0 | 548200.0 | 1997
RWE Npower | Great Eppleton RO | Wind | Onshore | No | Wind |  | 4.1 | LV | England | North East |  |  | 436900.0 | 548200.0 | 2010
RWE Npower | Great Yarmouth | Fossil Fuel | CCGT | No | Natural Gas |  | 420 | LV | England | Eastern | NR303PY |  | 652534.0 | 307744.0 | 2001
RWE Npower | Grimsby | Fossil Fuel | Single cycle | No | Natural Gas |  | 20 | LV | England | Yorkshire and Humber | DN312FW |  |  |  | 2018
RWE Npower | Grudie | Hydro | Natural Flow | No | Hydro |  | 2 | LV | Scotland | Scotland |  |  | 196459.0 | 867347.0 | 2017
RWE Npower | Gwynt y Mor | Wind | Offshore | No | Wind |  | 576 | HV | Wales | Wales |  | SH9482396924 | 292082.0 | 396482.0 | 2013
RWE Npower | Hameldon Hill | Wind | Onshore | No | Wind |  | 6 | LV | England | North West |  |  | 389495.0 | 432441.0 | 2006
RWE Npower | Hameldon Hill Extension | Wind | Onshore | No | Wind |  | 6 | LV | England | North West |  |  | 379914.0 | 430561.0 | 2013
RWE Npower | Hare Hill | Wind | Onshore | No | Wind |  | 2.3 | LV | England | North East |  |  | 442500.0 | 540500.0 | 2000
RWE Npower | Hare Hill RO | Wind | Onshore | No | Wind |  | 2.75 | LV | England | North East |  |  | 442500.0 | 540500.0 | 2004
RWE Npower | Haswell Moor Circuit 1 | Wind | Onshore | No | Wind |  | 5.15 | LV | England | North East |  |  | 438085.0 | 541365.0 | 2010
RWE Npower | Haswell Moor Circuit 2 | Wind | Onshore | No | Wind |  | 5.15 | LV | England | North East |  |  | 438085.0 | 541365.0 | 2010
RWE Npower | Hellrigg | Wind | Onshore | No | Wind |  | 9.2 | LV | England | North West |  |  | 313585.0 | 551775.0 | 2012
RWE Npower | High Head | Hydro | Natural Flow | No | Hydro |  | 17 | LV | Wales | Wales |  |  | 276927.54900200001 | 367625.06313700002 | 2002
RWE Npower | High Volts | Wind | Onshore | No | Wind |  | 2.3 | LV | England | North East |  |  | 445600.0 | 533500.0 | 2004
RWE Npower | High Volts RO | Wind | Onshore | No | Wind |  | 5.5 | LV | England | North East |  |  | 445200.0 | 533400.0 | 2004
RWE Npower | Holmside | Wind | Onshore | No | Wind |  | 2.3 | LV | England | North East |  |  | 420800.0 | 550300.0 | 2004
RWE Npower | Holmside RO | Wind | Onshore | No | Wind |  | 2.75 | LV | England | North East |  |  | 419500.0 | 552500.0 | 2004
RWE Npower | Humber Gateway | Wind | Offshore | No | Wind |  | 219 | HV | England | Yorkshire and Humber |  |  | 528439.0 | 411181.0 | 2015
RWE Npower | Hythe | Fossil Fuel | Single cycle | No | Natural Gas |  | 44 | LV | England | South East | SO453BP |  |  |  | 2005
RWE Npower | Inverbain | Hydro | Natural Flow | No | Hydro |  | 0.95 | LV | Scotland | Scotland |  |  | 178095.51863000001 | 856066.18485600001 | 2006
RWE Npower | Inverlael | Hydro | Natural Flow | No | Hydro |  | 2.5 | LV | Scotland | Scotland |  |  | 218208.41789700001 | 885467.82440599997 | 2009
RWE Npower | Kielder | Hydro | Natural Flow | No | Hydro |  | 6 | LV | England | North East |  |  | 369887.329501 | 587826.78962699999 | 2006
RWE Npower | Kiln Pit Hill | Wind | Onshore | No | Wind |  | 14 | LV | England | North East |  |  | 405590.0 | 554583.0 | 2011
RWE Npower | Kings Lynn | Fossil Fuel | CCGT | No | Natural Gas |  | 395 | LV | England | Eastern | PE343RD |  |  |  | 1997
RWE Npower | Knabs Ridge | Wind | Onshore | No | Wind |  | 16 | LV | England | Yorkshire and Humber |  |  | 423069.0 | 455946.0 | 2007
RWE Npower | Lindhurst | Wind | Onshore | No | Wind |  | 9 | LV | England | East Midlands |  |  | 456880.0 | 358150.0 | 2010
RWE Npower | Little Barford | Fossil Fuel | CCGT | No | Natural Gas |  | 723 | HV | England | Eastern | PE196YT |  | 519049.0 | 256838.0 | 1995
RWE Npower | Little Barford GT | Fossil Fuel | Single cycle | No | Diesel/Gas Oil |  | 17 | HV | England | East Midlands | PE196YT |  | 519049.0 | 256838.0 | 2006
RWE Npower | Little Cheyne Court | Wind | Onshore | No | Wind |  | 59.8 | LV | England | South East |  |  | 598310.0 | 122060.0 | 2008
RWE Npower | Lochelbank | Wind | Onshore | No | Wind |  | 9.6 | LV | Scotland | Scotland |  |  | 311440.0 | 713477.0 | 2010
RWE Npower | London Array | Wind | Offshore | No | Wind |  | 630 | HV | England | South East |  | TM459013 | 642078.0 | 197218.0 | 2013
RWE Npower | Low Head | Hydro | Natural Flow | No | Hydro |  | 14.98 | LV | Wales | Wales |  |  | 276927.54900200001 | 367625.06313700002 | 2002
RWE Npower | Maldie | Hydro | Natural Flow | No | Hydro |  | 4 | LV | Scotland | Scotland |  |  | 225150.0 | 934050.0 | 2013
RWE Npower | Markinch | Bioenergy | Bioenergy | Yes | Biomass |  | 65 | LV | Scotland | Scotland | KY76GU |  | 327988.0 | 701561.0 | 2014
RWE Npower | Middlemoor | Wind | Onshore | No | Wind |  | 54 | LV | England | North East |  |  | 414765.0 | 622786.0 | 2013
RWE Npower | Mynydd y Gwair | Wind | Onshore | No | Wind |  | 32.8 | HV | Wales | Wales |  |  | 265400.0 | 208320.0 | 2019
RWE Npower | North Hoyle | Wind | Offshore | No | Wind |  | 60 | LV | Wales | Wales |  | SJ0383892229 | 303823.0 | 392138.0 | 2004
RWE Npower | Novar 2 | Wind | Onshore | No | Wind |  | 36.8 | HV | Scotland | Scotland |  |  | 255500.0 | 871500.0 | 2012
RWE Npower | Out Newton (RO) | Wind | Onshore | No | Wind |  | 9.1 | LV | England | Yorkshire and Humber |  |  | 538800.0 | 421200.0 | 2002
RWE Npower | Pembroke | Fossil Fuel | CCGT | No | Natural Gas |  | 2199 | HV | Wales | Wales | SA715SS |  | 193370.0 | 200137.0 | 2012
RWE Npower | Rampion | Wind | Offshore | No | Wind |  | 400.2 | HV | England | South East |  |  | 525000.0 | 95000.0 | 2018
RWE Npower | Rhyl Flats | Wind | Offshore | No | Wind |  | 90 | LV | Wales | Wales |  | SH9024488299 | 290990.0 | 388002.0 | 2009
RWE Npower | River E | Hydro | Natural Flow | No | Hydro |  | 3 | LV | Scotland | Scotland |  |  | 251359.39736199999 | 818186.72195299994 | 2008
RWE Npower | Robin Rigg East | Wind | Offshore | No | Wind |  | 84 | HV | Scotland | Scotland |  |  | 291005.0 | 542348.0 | 2010
RWE Npower | Robin Rigg West | Wind | Offshore | No | Wind |  | 90 | HV | Scotland | Scotland |  |  | 288785.0 | 540522.0 | 2010
RWE Npower | Rosehall | Wind | Onshore | No | Wind |  | 24.7 | LV | Scotland | Scotland |  |  | 249550.0 | 903550.0 | 2013
RWE Npower | Scroby Sands | Wind | Offshore | No | Wind |  | 60 | LV | England | Eastern |  |  | 656417.0 | 311874.0 | 2004
RWE Npower | Selset | Hydro | Natural Flow | No | Hydro |  | 0.75 | LV | England | North East |  |  | 390300.0 | 521200.0 | 2010
RWE Npower | Stags Holt | Wind | Onshore | No | Wind |  | 20 | LV | England | Eastern |  |  | 544000.0 | 299000.0 | 2007
RWE Npower | Staythorpe | Fossil Fuel | CCGT | No | Natural Gas |  | 1828 | HV | England | East Midlands | NG235RQ |  | 475532.0 | 351265.0 | 2010
RWE Npower | The Hollies | Wind | Onshore | No | Wind |  | 2.6 | LV | England | East Midlands |  |  | 549995.0 | 362998.0 | 2008
RWE Npower | Triton Knoll | Wind | Offshore | No | Wind |  | 857 | HV | England | North East |  |  |  |  | 2021
RWE Npower | Tween Bridge | Wind | Onshore | No | Wind |  | 44 | LV | England | Yorkshire and Humber |  |  | 469324.0 | 416182.0 | 2012
Scira Offshore Energy | Dudgeon BMU 1 | Wind | Offshore | No | Wind |  | 108 | HV | England | Eastern |  |  | 575000.0 | 361000.0 | 2017
Scira Offshore Energy | Dudgeon BMU 2 | Wind | Offshore | No | Wind |  | 90 | HV | England | Eastern |  |  | 575000.0 | 361000.0 | 2017
Scira Offshore Energy | Dudgeon BMU 3 | Wind | Offshore | No | Wind |  | 102 | HV | England | Eastern |  |  | 575000.0 | 361000.0 | 2017
Scira Offshore Energy | Dudgeon BMU 4 | Wind | Offshore | No | Wind |  | 102 | HV | England | Eastern |  |  | 575000.0 | 361000.0 | 2017
Scira Offshore Energy | Hywind BMU 1 | Wind | Offshore | No | Wind |  | 30 | HV | Scotland | Scotland |  |  | 433500.0 | 846500.0 | 2017
Scira Offshore Energy | Sheringham Shoal BMU 1 | Wind | Offshore | No | Wind |  | 158 | HV | England | Eastern |  |  | 610671.0 | 364425.0 | 2012
Scira Offshore Energy | Sheringham Shoal BMU 2 | Wind | Offshore | No | Wind |  | 158 | HV | England | Eastern |  |  | 610671.0 | 364425.0 | 2012
Scottish Power | Arecleoch | Wind | Onshore | No | Wind |  | 120 | HV | Scotland | Scotland | KA260SJ |  | 221500.0 | 578500.0 | 2010
Scottish Power | Beinn an Tuirc I | Wind | Onshore | No | Wind |  | 29.7 | LV | Scotland | Scotland | PA286QY |  | 173950.0 | 636900.0 | 2002
Scottish Power | Beinn an Tuirc II | Wind | Onshore | No | Wind |  | 43.7 | HV | Scotland | Scotland | PA286QY |  | 173950.0 | 636900.0 | 2012
Scottish Power | Beinn an Tuirc III | Wind | Onshore | No | Wind |  | 49.95 | HV | Scotland | Scotland | PA286QY |  | 173950 | 636900 | 2021
Scottish Power | Beinn Tharsuinn | Wind | Onshore | No | Wind |  | 29.75 | HV | Scotland | Scotland | IV191LH |  | 261700.0 | 881900.0 | 2005
Scottish Power | Black Law I | Wind | Onshore | No | Wind |  | 124.2 | HV | Scotland | Scotland | ML118BW |  | 290998.0 | 653991.0 | 2005
Scottish Power | Black Law II | Wind | Onshore | No | Wind |  | 63.43 | HV | Scotland | Scotland | ML118EW |  | 289500.0 | 653500.0 | 2016
Scottish Power | Callagheen | Wind | Onshore | No | Wind |  | 16.9 | LV | Northern Ireland | Northern Ireland | BT934AL |  | 10820.0 | 521167.0 | 2006
Scottish Power | Carland Cross PV | Solar | PV | No | Solar |  | 10 | LV | England | South West | TR85JB |  |  |  | 2022
Scottish Power | Carland Cross RP | Wind | Onshore | No | Wind |  | 20 | LV | England | South West | TR85JB |  | 184500.0 | 54500.0 | 2013
Scottish Power | Clachan Flats | Wind | Onshore | No | Wind |  | 15.03 | HV | Scotland | Scotland | PA268BJ |  | 217950.0 | 714520.0 | 2009
Scottish Power | Coal Clough RP | Wind | Onshore | No | Wind |  | 16 | LV | England | North West | BB104RR |  | 390207.0 | 428154.0 | 2014
Scottish Power | Coldham | Wind | Onshore | No | Wind |  | 16 | LV | England | Eastern | PE14OLX |  | 525748.0 | 299048.0 | 2005
Scottish Power | Corkey | Wind | Onshore | No | Wind |  | 5 | LV | Northern Ireland | Northern Ireland | BT449JB |  | 126222.0 | 580523.0 | 1995
Scottish Power | Cruach Mhor | Wind | Onshore | No | Wind |  | 29.75 | LV | Scotland | Scotland | PA223AE |  | 203500.0 | 687500.0 | 2004
Scottish Power | Dersalloch | Wind | Onshore | No | Wind |  | 69 | HV | Scotland | Scotland | KA197NJ |  | 242500.0 | 603500.0 | 2016
Scottish Power | Dun Law I | Wind | Onshore | No | Wind |  | 17.16 | LV | Scotland | Scotland | TD26RA |  | 344600.0 | 657500.0 | 2000
Scottish Power | Dun Law II | Wind | Onshore | No | Wind |  | 29.75 | HV | Scotland | Scotland | TD26RA |  | 346582.0 | 657530.0 | 2009
Scottish Power | EA1 | Wind | Offshore | No | Wind |  | 714 | HV | England | Eastern |  |  |  |  | 2019
Scottish Power | Elliot's Hill | Wind | Onshore | No | Wind |  | 5 | LV | Northern Ireland | Northern Ireland | BT390TD |  | 134974.0 | 546006.0 | 1995
Scottish Power | Ewe Hill I | Wind | Onshore | No | Wind |  | 13.8 | LV | Scotland | Scotland | DG112QG |  | 315000.0 | 580000.0 | 2016
Scottish Power | Ewe Hill II | Wind | Onshore | No | Wind |  | 36.8 | HV | Scotland | Scotland | DG112QG |  | 315000.0 | 580000.0 | 2017
Scottish Power | Glenapp | Wind | Onshore | No | Wind |  | 22 | HV | Scotland | Scotland | KA260PG |  | 208000.0 | 573000.0 | 2017
Scottish Power | Green Knowes | Wind | Onshore | No | Wind |  | 27 | LV | Scotland | Scotland | FK147YJ |  | 296850.0 | 707550.0 | 2008
Scottish Power | Hagshaw Hill I | Wind | Onshore | No | Wind |  | 12 | LV | Scotland | Scotland | ML110RR |  | 278980.0 | 630740.0 | 1996
Scottish Power | Hagshaw Hill II | Wind | Onshore | No | Wind |  | 26 | LV | Scotland | Scotland | ML110RR |  | 278965.0 | 630750.0 | 2008
Scottish Power | Halsary | Wind | Onshore | No | Wind |  | 30 | HV | Scotland | Scotland | KW126UW |  |  |  | 2020
Scottish Power | Hare Hill I | Wind | Onshore | No | Wind |  | 13.2 | LV | Scotland | Scotland | KA184NW |  | 265320.0 | 609703.0 | 2000
Scottish Power | Hare Hill II | Wind | Onshore | No | Wind |  | 29.75 | HV | Scotland | Scotland | KA184NW |  | 265931.0 | 613982.0 | 2016
Scottish Power | Harestanes | Wind | Onshore | No | Wind |  | 136 | HV | Scotland | Scotland | DG111TU |  | 300000.0 | 595000.0 | 2013
Scottish Power | Kilgallioch | Wind | Onshore | No | Wind |  | 239 | HV | Scotland | Scotland | KA260RF |  | 223000.0 | 578000.0 | 2016
Scottish Power | Lynemouth | Wind | Onshore | No | Wind |  | 26 | LV | England | North East | NB639AT |  | 429400.0 | 589799.0 | 2012
Scottish Power | Mark Hill | Wind | Onshore | No | Wind |  | 56 | HV | Scotland | Scotland | KA260PX |  | 225000.0 | 585000.0 | 2011
Scottish Power | Middleton | Wind | Onshore | No | Wind |  | 12 | LV | Scotland | Scotland | G776PZ |  | 253158.0 | 656019.0 | 2013
Scottish Power | P&L | Wind | Onshore | No | Wind |  | 30.6 | LV | Wales | Wales | SY164BP |  | 302860.0 | 288543.0 | 1993
Scottish Power | Rigged Hill | Wind | Onshore | No | Wind |  | 5 | LV | Northern Ireland | Northern Ireland | BT490QJ |  | 90731.0 | 589745.0 | 1995
Scottish Power | Wether Hill | Wind | Onshore | No | Wind |  | 18.2 | LV | Scotland | Scotland | DG73UG |  | 270000.0 | 594000.0 | 2007
Scottish Power | Whitelee | Wind | Onshore | No | Wind |  | 322 | HV | Scotland | Scotland | KA36EX |  | 256800.0 | 645435.0 | 2007
Scottish Power | Whitelee II | Wind | Onshore | No | Wind |  | 217.02 | HV | Scotland | Scotland | KA36EX |  | 254220.0 | 640867.0 | 2012
Scottish Power | Wolf Bog | Wind | Onshore | No | Wind |  | 10 | LV | Northern Ireland | Northern Ireland | BT390TD |  | 137865.0 | 553129.0 | 2008
Sembcorp Utilities | Wilton 10 Biomass | Bioenergy | Bioenergy | Yes | Biomass |  | 33.276 | HV | England | North East | TS908WS |  | 456536.0 | 520395.0 | 2007
Sembcorp Utilities | Wilton 11 | Bioenergy | Bioenergy | No | MSW |  | 49 | HV | England | North East |  |  | 458191.0 | 520347.0 | 2016
Sembcorp Utilities | Wilton International | Fossil Fuel | Conventional steam | Yes | Natural Gas | Oil | 120 | HV | England | North East | TS908WS |  | 458275.0 | 517359.0 | 1952
SSE Group | Achanalt Power Station - A | Hydro | Natural Flow | No | Hydro |  | 3.1 | LV | Scotland | Scotland |  | NH309620 | 225895.0 | 861615.0 | 1956
SSE Group | Achany Windfarm | Wind | Onshore | No | Wind |  | 38 | LV | Scotland | Scotland |  | NC480018 | 252350.0 | 904150.0 | 2010
SSE Group | Aigas Power Station - A,E | Hydro | Natural Flow | No | Hydro |  | 20 | HV | Scotland | Scotland |  | NH474437 | 247395.0 | 843655.0 | 1962
SSE Group | Allt Na Lairige Power Station | Hydro | Natural Flow | No | Hydro |  | 6 | LV | Scotland | Scotland |  | NN231164 | 220655.0 | 714679.0 | 1956
SSE Group | Arnish | Fossil Fuel | Single Cycle | No | Diesel/Gas Oil |  | 10 | HV | Scotland | Scotland |  |  | 142229.0 | 930499.0 | 2000
SSE Group | Artfield Fell Windfarm - A,C | Wind | Onshore | No | Wind |  | 28.6 | LV | Scotland | Scotland |  | NX236659 | 223005.0 | 567000.0 | 2005
SSE Group | Awe Barrage - A | Hydro | Natural Flow | No | Hydro |  | 0.886 | LV | Scotland | Scotland |  | NN046287 | 202987.0 | 729485.0 | 1956
SSE Group | Barra | Fossil Fuel | Single Cycle | No | Diesel/Gas Oil |  | 2.5 | HV | Scotland | Scotland | HS95YA |  | 71706.0 | 803309.0 | 1986
SSE Group | Beannachran Dam - A | Hydro | Natural Flow | No | Hydro |  | 0.16 | LV | Scotland | Scotland |  | NN325394 | 233926.125814 | 831784.38433300005 | 1951
SSE Group | Beatrice Offshore windfarm | Wind | Offshore | No | Wind |  | 588 | HV | Scotland | Scotland |  | ND500486 | 344074.0 | 911416.0 | 2018
SSE Group | Bessy Bell Windfarm | Wind | Onshore | No | Wind |  | 5 | LV | Northern Ireland | Northern Ireland | BT784EZ |  | 49687.0 | 547922.0 | 1995
SSE Group | Bessy Bell Windfarm (NI) Limited | Wind | Onshore | No | Wind |  | 9 | LV | Northern Ireland | Northern Ireland | H395815 |  | 51953.0 | 543825.0 | 2008
SSE Group | Bhlaraidh Wind Farm | Wind | Onshore | No | Wind |  | 110.4 | HV | Scotland | Scotland |  | NH369203 | 238277.0 | 816488.0 | 2017
SSE Group | Bowmore | Fossil Fuel | Single Cycle | No | Diesel/Gas Oil |  | 6 | HV | Scotland | Scotland | PA437LL |  | 132024.0 | 660214.0 | 1946
SSE Group | Burghfield | Fossil Fuel | Single cycle | No | Natural Gas |  | 50 | HV | England | South East | RG303UW |  | 466926.0 | 166323.0 | 1998
SSE Group | Cashlie Power Station - A,C | Hydro | Natural Flow | No | Hydro |  | 11 | LV | Scotland | Scotland |  | NN507421 | 248530.0 | 741735.0 | 1959
SSE Group | Cassley Power Station - A,C,E | Hydro | Natural Flow | No | Hydro |  | 10 | LV | Scotland | Scotland |  | NC396232 | 247325.0 | 901540.0 | 1959
SSE Group | Cathkin Braes Wind Farm | Wind | Onshore | No | Wind |  | 3 | LV | Scotland | Scotland |  | NS612582 | 261220.0 | 658203.0 | 2013
SSE Group | Ceannacroc Compensation Generator | Hydro | Natural Flow | No | Hydro |  | 3.5 | LV | Scotland | Scotland |  | NH224108 | 222745.0 | 810690.0 | 1956
SSE Group | Ceannacroc Power Station - A, E | Hydro | Natural Flow | No | Hydro |  | 16.5 | LV | Scotland | Scotland |  | NH224108 | 222745.0 | 810690.0 | 1956
SSE Group | Chickerell | Fossil Fuel | Single cycle | No | Natural Gas |  | 50 | HV | England | South West | DT49XH |  | 364051.0 | 80933.0 | 1998
SSE Group | Chippenham | Fossil Fuel | Single cycle | No | Natural Gas |  | 10.07 | HV | England | South West | SN151RS |  | 391412.0 | 173455.0 | 2002
SSE Group | Chliostair Power Station - A,C | Hydro | Natural Flow | No | Hydro |  | 1.32 | LV | Scotland | Scotland |  | NB059092 | 120328.967017 | 908665.53669900005 | 1960
SSE Group | Clachan | Hydro | Natural Flow | No | Hydro |  | 40 | LV | Scotland | Scotland |  | NN192133 | 148598.006933 | 866496.66653699998 | 1955
SSE Group | Cladach Dam | Hydro | Natural Flow | No | Hydro |  | 0.22 | LV | Scotland | Scotland |  | NS014376 | 219715.0 | 595201.0 | 1949
SSE Group | Cluanie Dam - A | Hydro | Natural Flow | No | Hydro |  | 0.32 | LV | Scotland | Scotland |  | NH185099 | 218164.204031 | 809842.51726600004 | 1956
SSE Group | Clunie | Hydro | Natural Flow | No | Hydro |  | 61.2 | HV | Scotland | Scotland | PH165NF |  | 293345.89585299999 | 757790.00295600004 | 1950
SSE Group | Clunie Dam - A | Hydro | Natural Flow | No | Hydro |  | 0.175 | LV | Scotland | Scotland |  | NN884603 | 293345.89585299999 | 757790.00295600004 | 1950
SSE Group | Clyde Windfarm (Central) | Wind | Onshore | No | Wind |  | 195.9 | LV | Scotland | Scotland |  | NS987202 | 302500.0 | 622500.0 | 2011
SSE Group | Clyde Windfarm (North) | Wind | Onshore | No | Wind |  | 197.7 | LV | Scotland | Scotland |  | NS985240 | 302500.0 | 627500.0 | 2012
SSE Group | Clyde Windfarm (South) | Wind | Onshore | No | Wind |  | 128.8 | LV | Scotland | Scotland |  | NS982134 | 302500.0 | 617500.0 | 2011
SSE Group | Cuaich Power Station - A,C | Hydro | Natural Flow | No | Hydro |  | 2.5 | LV | Scotland | Scotland |  | NN574868 | 263487.841273 | 784203.521908 | 1959
SSE Group | Culligran Comp Set - A,C,E | Hydro | Natural Flow | No | Hydro |  | 2 | HV | Scotland | Scotland |  | NH378405 | 231877.310669 | 839888.30312599998 | 1962
SSE Group | Culligran Power Station Unit 2 - A | Hydro | Natural Flow | No | Hydro |  | 17.1 | HV | Scotland | Scotland |  | NH378405 | 231877.310669 | 839888.30312599998 | 1962
SSE Group | Dalchonize Power Station-A,C | Hydro | Natural Flow | No | Hydro |  | 4 | LV | Scotland | Scotland |  | NN740220 | 274035.0 | 721990.0 | 1958
SSE Group | Deanie | Hydro | Natural Flow | No | Hydro |  | 38 | HV | Scotland | Scotland | IV47JX |  | 219200.00004499999 | 710099.99998600001 | 1963
SSE Group | Dinorwig | Pumped hydro | Pumped hydro | No | Pumped hydro |  | 1800 | HV | Wales | Wales |  | SH594600 | 259400.0 | 360000.0 | 1984
SSE Group | Drumderg Windfarm | Wind | Onshore | No | Wind |  | 36.8 | LV | Scotland | Scotland |  | NO180538 | 324500.0 | 748500.0 | 2008
SSE Group | Duchally Power Station - A,C,E | Hydro | Natural Flow | No | Hydro |  | 0.45 | LV | Scotland | Scotland |  | NC368203 | 238694.128218 | 916750.91899200005 | 1959
SSE Group | Dundreggan Dam A | Hydro | Natural Flow | No | Hydro |  | 0.16 | LV | Scotland | Scotland |  | NH357156 | 231413.082559 | 813651.70164300001 | 1953
SSE Group | Dunmaglass Wind Farm | Wind | Onshore | No | Wind |  | 94.05 | HV | Scotland | Scotland |  | NH609227 | 264000.0 | 820120.0 | 2016
SSE Group | Errochty | Hydro | Natural Flow | No | Hydro |  | 75 | HV | Scotland | Scotland | PH165SD |  | 280853.25648699998 | 765408.19507100002 | 1955
SSE Group | Fairburn Windfarm | Wind | Onshore | No | Wind |  | 40 | LV | Scotland | Scotland |  | NH426534 | 242550.0 | 852250.0 | 2009
SSE Group | Fasnakyle | Hydro | Natural Flow | No | Hydro |  | 69 | HV | Scotland | Scotland |  | NH319296 | 226977.973512 | 827215.18281999999 | 1951
SSE Group | Fasnakyle Compensation Generator - A, C | Hydro | Natural Flow | No | Hydro |  | 7.701 | LV | Scotland | Scotland |  | NH319296 | 226977.973512 | 827215.18281999999 | 2006
SSE Group | Finlarig Power Station - A,G | Hydro | Natural Flow | No | Hydro |  | 16.5 | HV | Scotland | Scotland |  | NN585345 | 257077.347893 | 733907.81862599996 | 1955
SSE Group | Foyers Falls Power Station | Hydro | Natural Flow | No | Hydro |  | 5.2 | LV | Scotland | Scotland |  | NH497210 | 249845.0 | 820010.0 | 1968
SSE Group | Gaur Power Station - A | Hydro | Natural Flow | No | Hydro |  | 7.9 | LV | Scotland | Scotland |  | NN464579 | 247261.333874 | 757140.631283 | 1953
SSE Group | Gisla Power Station - A | Hydro | Natural Flow | No | Hydro |  | 0.72 | LV | Scotland | Scotland |  | NB129258 | 113291.038795 | 926162.88476399996 | 1960
SSE Group | Glendoe Hydro Power Station | Hydro | Natural Flow | No | Hydro |  | 100 | HV | Scotland | Scotland |  | NH406079 | 238719.406541 | 808777.04899200005 | 2008
SSE Group | Glenmoriston | Hydro | Natural Flow | No | Hydro |  | 37 | HV | Scotland | Scotland | IV36YH |  | 230869.824876 | 812928.10700800002 | 1957
SSE Group | Gordonbush Ext | Wind | Onshore | No | Wind |  | 47.3 | HV | Scotland | [5 empty] | 2021
SSE Group | Gordonbush Wind Farm | Wind | Onshore | No | Wind |  | 70 | HV | Scotland | Scotland |  | NC826113 | 284500.0 | 909500.0 | 2011
SSE Group | Greater Gabbard | Wind | Offshore | No | Wind |  | 504 | HV | England | Eastern |  | TM714315 | 670237.0 | 231640.0 | 2011
SSE Group | Griffin Wind Farm | Wind | Onshore | No | Wind |  | 188.6 | HV | Scotland | Scotland |  | NN910427 | 293600.0 | 744600.0 | 2011
SSE Group | Grudie Bridge Power Station - A, G | Hydro | Natural Flow | No | Hydro |  | 18.66 | LV | Scotland | Scotland |  | NH310624 | 231315.68004800001 | 862293.36975099996 | 1950
SSE Group | Hadyard Hill Windfarm - A,C | Wind | Onshore | No | Wind |  | 119.8 | HV | Scotland | Scotland |  | NX279982 | 227133.0 | 597446.0 | 2005
SSE Group | Inverawe | Hydro | Natural Flow | No | Hydro |  | 25 | LV | Scotland | Scotland | PA351HQ |  | 202299.54597899999 | 730929.48161799996 | 1963
SSE Group | Invergarry Dam - A, E | Hydro | Natural Flow | No | Hydro |  | 0.24 | LV | Scotland | Scotland |  | NH319413 | 238862.965222 | 809324.00929800002 | 2003
SSE Group | Invergarry Power Station - A,E | Hydro | Natural Flow | No | Hydro |  | 19.975 | HV | Scotland | Scotland |  | NH319013 | 231930.0 | 801320.0 | 1956
SSE Group | Keadby | Fossil Fuel | CCGT | No | Natural Gas |  | 735 | HV | England | East Midlands | DN173EF |  | 483280.0 | 411671.0 | 1982
SSE Group | Keadby Wind Farm | Wind | Onshore | No | Wind |  | 68 | LV | England | Yorkshire and Humber |  | SE829126 | 481890.0 | 413515.0 | 2013
SSE Group | Kerry Falls Power Station | Hydro | Natural Flow | No | Hydro |  | 1.25 | LV | Scotland | Scotland |  | NG829720 | 181231.12067100001 | 875180.63170899998 | 1951
SSE Group | Kilmelford Compset A,C | Hydro | Natural Flow | No | Hydro |  | 0.082 | LV | Scotland | Scotland |  | NM541144 | 183921.68693900001 | 712587.00644599996 | 1956
SSE Group | Kilmelford Power Station - A, C, | Hydro | Natural Flow | No | Hydro |  | 2 | LV | Scotland | Scotland |  | NM541144 | 183921.68693900001 | 712587.00644599996 | 1956
SSE Group | Kilmorack Power Station -A,E | Hydro | Natural Flow | No | Hydro |  | 20 | HV | Scotland | Scotland |  | NH494442 | 249410.0 | 844225.0 | 1962
SSE Group | Kingairloch Power Station - A,C | Hydro | Natural Flow | No | Hydro |  | 3.5 | LV | Scotland | Scotland |  | NM810547 | 184177.03533499999 | 752489.46736999997 | 2005
SSE Group | Kirkwall | Fossil Fuel | Single Cycle | No | Diesel/Gas Oil |  | 16 | HV | Scotland | Scotland | KW151AN |  | 344667.0 | 1010985.0 | 1952
SSE Group | Lairg Power Station | Hydro | Natural Flow | No | Hydro |  | 3.5 | LV | Scotland | Scotland |  | NC575070 | 249712.919287 | 916014.00856600003 | 1959
SSE Group | Lednock Power Station - A | Hydro | Natural Flow | No | Hydro |  | 3 | LV | Scotland | Scotland |  | NN698304 | 276730.0 | 722040.0 | 1961
SSE Group | Lerwick | Fossil Fuel | Single cycle | No | Diesel/Gas Oil |  | 67 | LV | Scotland | Scotland | ZE10PS |  | 446456.0 | 1142790.0 | 1953
SSE Group | Livishie Power Station - A | Hydro | Natural Flow | No | Hydro |  | 15 | LV | Scotland | Scotland |  | NH353160 | 240245.0 | 817495.0 | 1962
SSE Group | Loch Carnan | Fossil Fuel | Single Cycle | No | Diesel/Gas Oil |  | 11 | HV | Scotland | Scotland |  |  | 83233.0 | 842636.0 | 1972
SSE Group | Loch Dubh | Hydro | Natural Flow | No | Hydro |  | 1.2 | LV | Scotland | Scotland |  | NC149012 | 213243.84406900001 | 901138.944043 | 1954
SSE Group | Loch Ericht Power Station - A | Hydro | Natural Flow | No | Hydro |  | 2.2 | LV | Scotland | Scotland |  | NN553728 | 262079.87718099999 | 783677.43128999998 | 1962
SSE Group | Loch Gair Power Station - A,C | Hydro | Natural Flow | No | Hydro |  | 6 | LV | Scotland | Scotland |  | NR925908 | 192865.0 | 691305.0 | 1961
SSE Group | Lochay | Hydro | Natural Flow | No | Hydro |  | 46 | HV | Scotland | Scotland |  | NN545350 | 256968.202407 | 734182.06732699997 | 1958
SSE Group | Lochay Compensation Generator | Hydro | Natural Flow | No | Hydro |  | 2 | LV | Scotland | Scotland |  | NN545350 | 258746.51913299999 | 733924.38001600001 | 1958
SSE Group | Lochay Fish Pass Generator - C | Hydro | Natural Flow | No | Hydro |  | 0.054 | LV | Scotland | Scotland |  | NN545350 | 256968.202407 | 734182.06732699997 | 1958
SSE Group | Loyne Power Station - A,C | Hydro | Natural Flow | No | Hydro |  | 0.55 | LV | Scotland | Scotland |  | NH200079 | 228554.88977000001 | 813307.01867400005 | 1956
SSE Group | Lubreoch Power Station - A | Hydro | Natural Flow | No | Hydro |  | 4 | LV | Scotland | Scotland |  | NN454418 | 245250.958315 | 741685.36456999998 | 1958
SSE Group | Luichart | Hydro | Natural Flow | No | Hydro |  | 34 | HV | Scotland | Scotland | IV149EW |  | 231809.687121 | 862261.33658100001 | 1954
SSE Group | Luichart Dam - A | Hydro | Natural Flow | No | Hydro |  | 0.085 | LV | Scotland | Scotland |  | NH389579 | 232652.83906500001 | 862232.74855599995 | 1954
SSE Group | Lussa Power Station - A | Hydro | Natural Flow | No | Hydro |  | 2.4 | LV | Scotland | Scotland |  | NR735261 | 176153.721105 | 625756.90955900005 | 1952
SSE Group | Medway | Fossil Fuel | CCGT | No | Natural Gas |  | 755 | HV | England | South East | ME30AG |  | 586916.0 | 174008.0 | 1995
SSE Group | Meig Dam | Hydro | Natural Flow | No | Hydro |  | 0.076 | LV | Scotland | Scotland |  | NH375560 | 237124.664659 | 855942.36082399997 | 1954
SSE Group | Misgeach Power Station - A | Hydro | Natural Flow | No | Hydro |  | 0.35 | LV | Scotland | Scotland |  | NH183381 | 229571.01829800001 | 838608.37607100001 | 1963
SSE Group | Morar Power Station - A,C | Hydro | Natural Flow | No | Hydro |  | 0.75 | LV | Scotland | Scotland |  | NM682922 | 168582.025887 | 792663.62937500002 | 1950
SSE Group | Mossford Power Station - A,G | Hydro | Natural Flow | No | Hydro |  | 18.66 | HV | Scotland | Scotland |  | NH330633 | 233010.426393 | 863187.36691300001 | 1957
SSE Group | Mucomir Power Station | Hydro | Natural Flow | No | Hydro |  | 1.9 | LV | Scotland | Scotland |  | NN183838 | 218350.0 | 783900.0 | 1962
SSE Group | Mullardoch Power Station - A,C | Hydro | Natural Flow | No | Hydro |  | 2.4 | LV | Scotland | Scotland |  | NH223310 | 222860.0 | 831415.0 | 1955
SSE Group | Nant Power Station - A,E | Hydro | Natural Flow | No | Hydro |  | 15 | HV | Scotland | Scotland |  | NN016207 | 203606.80395999999 | 723291.404201 | 1963
SSE Group | Nostie Bridge Power Station - A | Hydro | Natural Flow | No | Hydro |  | 1.3 | LV | Scotland | Scotland |  | NH852274 | 185143.85883700001 | 826708.608687 | 1950
SSE Group | Orrin Dam - A | Hydro | Natural Flow | No | Hydro |  | 0.256 | LV | Scotland | Scotland |  | NH403503 | 245505.394088 | 856091.61578800005 | 2002
SSE Group | Orrin Power Station- A | Hydro | Natural Flow | No | Hydro |  | 18 | HV | Scotland | Scotland |  | NH436546 | 246905.0 | 851695.0 | 1959
SSE Group | Peterhead | Fossil Fuel | CCGT | No | Natural Gas |  | 1180 | HV | Scotland | Scotland | AB423BZ |  | 412790.0 | 843093.0 | 1980
SSE Group | Pitlochry Compensation Generation - A | Hydro | Natural Flow | No | Hydro |  | 0.059 | LV | Scotland | Scotland |  | NN936577 | 293500.038046 | 757752.01422899996 | 1950
SSE Group | Pitlochry Power Station - A | Hydro | Natural Flow | No | Hydro |  | 15 | HV | Scotland | Scotland |  | NN936577 | 293515.0 | 757730.0 | 1950
SSE Group | Quoich Dam - A | Hydro | Natural Flow | No | Hydro |  | 0.32 | LV | Scotland | Scotland |  | NH071023 | 216881.84323299999 | 800852.89049599995 | 1955
SSE Group | Quoich Power Station - A, E, G | Hydro | Natural Flow | No | Hydro |  | 18.05 | LV | Scotland | Scotland |  | NH107012 | 216881.8432 | 800852.89049999998 | 1955
SSE Group | Rannoch | Hydro | Natural Flow | No | Hydro |  | 45 | LV | Scotland | Scotland | PH173QP |  | 265618.90567399998 | 758237.41850399994 | 1930
SSE Group | River Cuileig | Hydro | Natural Flow | No | Hydro |  | 3.3 | LV | Scotland | Scotland |  | NH193789 | 219300.0 | 878900.0 | 2002
SSE Group | Seagreen | Wind | Offshore | No | Wind |  | 759 |  | Scotland | Scotland |  | NO399369 |  |  | 2022
SSE Group | Shin Diversion Dam - A | Hydro | Natural Flow | No | Hydro |  | 0.1 | LV | Scotland | Scotland |  | NC582051 | 257261.32734300001 | 897258.47946900001 | 1958
SSE Group | Shin Power Station-A,G | Hydro | Natural Flow | No | Hydro |  | 18.62 | LV | Scotland | Scotland |  | NH574974 | 257261.32734300001 | 897258.47946900001 | 1958
SSE Group | Slieve Kirk Windfarm | Wind | Onshore | No | Wind |  | 73.6 | HV | Northern Ireland | Northern Ireland | BT473RL |  | 61258.0 | 571215.0 | 2011
SSE Group | Slough Heat & Power | Bioenergy | Bioenergy | Yes | Biomass |  | 20 | LV | England | South East | SL14TT |  | 495316.0 | 181476.0 | 2014
SSE Group | Sloy | Hydro | Natural Flow | No | Hydro |  | 152.5 | HV | Scotland | Scotland | G837DP |  | 232178.80345499999 | 709714.41867299995 | 1950
SSE Group | Spurness Wind Farm II | Wind | Onshore | No | Wind |  | 10 | LV | Scotland | Scotland |  | HY606356 | 360531.0 | 1033828.0 | 2012
SSE Group | Sron Mor Power Station - A,C | Hydro | Natural Flow | No | Hydro |  | 5 | LV | Scotland | Scotland |  | NN161201 | 264850.0 | 798415.0 | 1957
SSE Group | SSE Arena Belfast | Solar | PV | No | Solar |  | 0.41992 | LV | Northern Ireland | Northern Ireland |  | NW473302 | 147232.0 | 530243.0 | 2017
SSE Group | St Fillans Power Station - A, G | Hydro | Natural Flow | No | Hydro |  | 16.83 | LV | Scotland | Scotland |  | NN691246 | 269101.60388900002 | 724133.42061899998 | 1957
SSE Group | Stornoway | Fossil Fuel | Single Cycle | No | Diesel/Gas Oil |  | 23 | HV | Scotland | Scotland |  |  | 143150.0 | 932158.0 | 1952
SSE Group | Storr Lochs Power Station - A | Hydro | Natural Flow | No | Hydro |  | 2.4 | LV | Scotland | Scotland |  | NG515527 | 147915.64170899999 | 843505.35491899995 | 1952
SSE Group | Strathy North | Wind | Onshore | No | Wind |  | 66 | HV | Scotland | Scotland |  | NC820598 | 281550.0 | 957550.0 | 2015
SSE Group | Striven Power Station - A | Hydro | Natural Flow | No | Hydro |  | 8 | LV | Scotland | Scotland |  | NS056840 | 205595.0 | 683990.0 | 1951
SSE Group | Stronelairg Wind Farm | Wind | Onshore | No | Wind |  | 227.7 | HV | Scotland | Scotland |  | NH526030 | 247166.0 | 806833.0 | 2018
SSE Group | Stronuich Power Station - A | Hydro | Natural Flow | No | Hydro |  | 0.18 | LV | Scotland | Scotland |  | NN507419 | 250616.896446 | 742103.88824100001 | 1957
SSE Group | Tangy Wind Farm - A | Wind | Onshore | No | Wind |  | 18.52 | LV | Scotland | Scotland |  | NR685282 | 167373.0 | 626330.0 | 2002
SSE Group | Thatcham | Fossil Fuel | Single cycle | No | Diesel/Gas Oil |  | 9 | HV | England | South East | RG194PP |  | 451330.0 | 157079.0 | 1994
SSE Group | Tievenameenta Wind Farm | Wind | Onshore | No | Wind |  | 34.5 | LV | Northern Ireland | Northern Ireland |  | NV288423 | 28892.0 | 543668.0 | 2016
SSE Group | Tiree | Fossil Fuel | Single Cycle | No | Diesel/Gas Oil |  | 2.5 | HV | Scotland | Scotland | PA776UP |  | 100030.0 | 744120.0 | 1953
SSE Group | Toddleburn Windfarm | Wind | Onshore | No | Wind |  | 27.6 | HV | Scotland | Scotland |  | NT433499 | 345050.0 | 653150.0 | 2010
SSE Group | Torr Achilty Power Station - A,E | Hydro | Natural Flow | No | Hydro |  | 15 | LV | Scotland | Scotland |  | NH446545 | 244418.37481199999 | 854546.61670599994 | 1954
SSE Group | Tralaig Power Station | Hydro | Natural Flow | No | Hydro |  | 0.084 | LV | Scotland | Scotland |  | NM871169 | 183921.68693900001 | 712587.00644599996 | 1956
SSE Group | Trinafour Power Station - A | Hydro | Natural Flow | No | Hydro |  | 0.55 | LV | Scotland | Scotland |  | NN725648 | 270988.13688900002 | 765725.19146 | 1959
SSE Group | Tummel | Hydro | Natural Flow | No | Hydro |  | 34 | LV | Scotland | Scotland | PH165SB |  | 261249.15323600001 | 580838.54599699995 | 1933
SSE Group | Vaich Power Station | Hydro | Natural Flow | No | Hydro |  | 0.32 | LV | Scotland | Scotland |  | NH321726 | 234419.67884499999 | 875106.58660599997 | 1956
Statkraft | Alltwalis | Wind | Onshore | No | Wind |  | 23 | HV | Wales | Wales | SA327ED |  | 246387.0 | 233404.0 | 2009
Statkraft | Andershaw | Wind | Onshore | No | Wind |  | 35 | HV | Scotland | Scotland | ML126SX |  | 283500.0 | 625500.0 | 2017
Statkraft | Baillie | Wind | Onshore | No | Wind |  | 53 | HV | Scotland | Scotland | KW147EP |  | 302550.0 | 965650.0 | 2013
Statkraft | Berry Burn | Wind | Onshore | No | Wind |  | 67 | HV | Scotland | Scotland | IV362QH |  | 311550.0 | 840550.0 | 2014
Statkraft | Rheidol Hydro Scheme Gen 1 | Hydro | Natural Flow | No | Hydro |  | 13.5 | LV | Wales | Wales |  |  | 270466.35895199998 | 279169.77504799998 | 1962
Statkraft | Rheidol Hydro Scheme Gen 2 | Hydro | Natural Flow | No | Hydro |  | 20.5 | LV | Wales | Wales |  |  | 274692.23303100001 | 283465.92701300001 | 1962
Statkraft | Rheidol Hydro Scheme Gen 3 | Hydro | Natural Flow | No | Hydro |  | 20.5 | LV | Wales | Wales |  |  | 274692.23303100001 | 283465.92701300001 | 1962
Statkraft | Rheidol Hydro Scheme Gen 4 | Hydro | Natural Flow | No | Hydro |  | 1.25 | LV | Wales | Wales |  |  | 270704.12983400002 | 279283.03561399999 | 1961
Statkraft | Rheidol Hydro Scheme Gen 5 | Hydro | Natural Flow | No | Hydro |  | 0.075 | LV | Wales | Wales |  |  | 275303.156097 | 283745.93445200002 | 1963
Statkraft | Rheidol Hydro Scheme Gen 6 | Hydro | Natural Flow | No | Hydro |  | 0.05 | LV | Wales | Wales |  |  | 274692.23303100001 | 283465.92701300001 | 1963
Statkraft | Rheidol Hydro Scheme Gen 7 | Hydro | Natural Flow | No | Hydro |  | 0.1 | LV | Wales | Wales |  |  | 270704.12983400002 | 279283.03561399999 | 1985
Temporis Capital | Achairn | Wind | Onshore | No | Wind |  | 6 | LV | Scotland | Scotland | KW15SG |  | 329950.0 | 950650.0 | 2009
Temporis Capital | Biggleswade | Wind | Onshore | No | Wind |  | 20 | LV | England | Eastern | SG189TA |  | 521653.0 | 240193.0 | 2013
Temporis Capital | Blackcraig | Wind | Onshore | No | Wind |  | 52.9 | HV | Scotland | Scotland | DG73DZ |  | 270500.0 | 582500.0 | 2018
Temporis Capital | Craig | Wind | Onshore | No | Wind |  | 10 | HV | Scotland | Scotland | DG130NZ |  | 331995.0 | 586055.0 | 2007
Temporis Capital | Craig 2 | Wind | Onshore | No | Wind |  | 4.7 | HV | Scotland | Scotland | DG130NZ |  | 333264.0 | 587956.0 | 2017
Temporis Capital | Derrydarroch | Hydro | Natural Flow | No | Hydro |  | 1.995 | LV | Scotland | Scotland | G837DX |  | 212176.0 | 775418.0 | 2015
Temporis Capital | Dunsland Cross | Wind | Onshore | No | Wind |  | 6.15 | LV | England | South West | EX227AW |  | 242041.0 | 107244.0 | 2017
Temporis Capital | Eye | Wind | Onshore | No | Wind |  | 6.8 | LV | England | Eastern | SG189TA |  | 613137.0 | 274854.0 | 2014
Temporis Capital | Greendykeside | Wind | Onshore | No | Wind |  | 4 | LV | Scotland | Scotland | ML67TT |  | 281134.0 | 670403.0 | 2007
Temporis Capital | Halesworth | Wind | Onshore | No | Wind |  | 10 | LV | England | Eastern | IP198NH |  | 640461.0 | 278558.0 | 2015
Temporis Capital | Lochhead | Wind | Onshore | No | Wind |  | 6 | LV | Scotland | Scotland | ML93PP |  | 275500.0 | 646500.0 | 2009
Temporis Capital | Muirhall | Wind | Onshore | No | Wind |  | 12.3 | LV | Scotland | Scotland | EH558LN |  | 300605.0 | 653760.0 | 2010
Temporis Capital | Newark | Wind | Onshore | No | Wind |  | 6 | LV | England | East Midlands | NG243SD |  | 479589.0 | 350765.0 | 2017
Temporis Capital | Osspower | Hydro | Natural Flow | No | Hydro |  | 1.995 | LV | Scotland | Scotland | G837DX |  | 0.0 | 0.0 | 2012
Temporis Capital | Pickenham | Wind | Onshore | No | Wind |  | 4 | LV | England | Eastern | PE378JX |  | 585114.0 | 306597.0 | 2014
Temporis Capital | Ransonmoor | Wind | Onshore | No | Wind |  | 17.8 | LV | England | Eastern | PE150TY |  | 537950.0 | 292470.0 | 2007
Temporis Capital | Tullymurdoch | Wind | Onshore | No | Wind |  | 14.4 | LV | Scotland | Scotland | PH118LH |  | 319575.0 | 752228.0 | 2018
Temporis Capital | Upper Falloch | Hydro | Natural Flow | No | Hydro |  | 0.896 | LV | Scotland | Scotland | FK208RL |  | 0.0 | 0.0 | 2015
Temporis Capital | Weston | Wind | Onshore | No | Wind |  | 4 | LV | England | Eastern | PE378JX |  | 609009.0 | 315326.0 | 2014
Temporis Capital | White Mill | Wind | Onshore | No | Wind |  | 14.35 | LV | England | Eastern | PE140LX |  | 545100.0 | 301570.0 | 2012
The Banks Group | Armistead Wind Farm | Wind | Onshore | No | Wind |  | 12.3 | LV | England | North West | LA80HT |  |  |  | 2013
The Banks Group | Hazlehead Wind Farm | Wind | Onshore | No | Wind |  | 6.15 | LV | England | Yorkshire and Humber | HD92TR |  |  |  | 2011
The Banks Group | Heysham South Wind Farm | Wind | Onshore | No | Wind |  | 7.5 | LV | England | North West | LA33ES |  |  |  | 2015
The Banks Group | Hook Moor Wind Farm | Wind | Onshore | No | Wind |  | 10 | LV | England | Yorkshire and Humber | LS253EB |  |  |  | 2016
The Banks Group | Kype Muir Wind Farm | Wind | Onshore | No | Wind |  | 88.4 | HV | Scotland | Scotland | ML106RE |  | 268129.0 | 640258.0 | 2019
The Banks Group | Lambs Hill Wind Farm | Wind | Onshore | No | Wind |  | 8 | LV | England | North East | TS211LX |  |  |  | 2017
The Banks Group | Marr Wind Farm | Wind | Onshore | No | Wind |  | 8.2 | LV | England | Yorkshire and Humber | DN57AZ |  |  |  | 2012
The Banks Group | Middle Muir Wind Farm | Wind | Onshore | No | Wind |  | 51 | HV | Scotland | Scotland | ML126SZ |  | 288964.0 | 625283.0 | 2018
The Banks Group | Moor House Wind Farm | Wind | Onshore | No | Wind |  | 12 | LV | England | North East | DL21SN |  |  |  | 2018
The Banks Group | Penny Hill Wind Farm | Wind | Onshore | No | Wind |  | 20.4 | LV | England | Yorkshire and Humber | S669BH |  |  |  | 2013
Toucan Energy Services | Aston House | Solar | PV | No | Solar |  | 19.8266 | LV | England | East Midlands |  | DE65AG | 416833.0 | 331778.0 | 2015
Toucan Energy Services | Balcombe | Solar | PV | No | Solar |  | 4.9608 | LV | England | South East | RH194QS |  | 535377.0 | 132854.0 | 2016
Toucan Energy Services | Bentham | Solar | PV | No | Solar |  | 11.051 | LV | England | South West | SN54JB |  | 407114.0 | 189633.0 | 2015
Toucan Energy Services | Bluegates | Solar | PV | No | Solar |  | 10.6972 | LV | England | Eastern | CO78DE |  | 607018.0 | 222279.0 | 2015
Toucan Energy Services | Burnham Wick | Solar | PV | No | Solar |  | 4.9992 | LV | England | Eastern | CM08LU |  | 596876.0 | 195875.0 | 2015
Toucan Energy Services | Canopus | Solar | PV | No | Solar |  | 4.9986 | LV | England | East Midlands | PE227BE |  | 530597.0 | 347613.0 | 2015
Toucan Energy Services | Carrowdore | Solar | PV | No | Solar |  | 5.9816 | LV | Northern Ireland | Northern Ireland | BT222HH |  | 169400.0 | 525454.0 | 2017
Toucan Energy Services | Chapel Hill | Solar | PV | No | Solar |  | 10.0703 | LV | Wales | Wales | SA715HY |  | 196092.0 | 197842.0 | 2015
Toucan Energy Services | Cranham | Solar | PV | No | Solar |  | 2.9987 | LV | England | London | RM143NU |  | 558400.0 | 187089.0 | 2016
Toucan Energy Services | Dunkeswell | Solar | PV | No | Solar |  | 2.7951 | LV | England | South West |  | EX144RD | 313746.0 | 107938.0 | 2015
Toucan Energy Services | Eckland Lodge | Solar | PV | No | Solar |  | 3.657 | LV | England | East Midlands | LE168HB |  | 478672.0 | 284948.0 | 2016
Toucan Energy Services | Five Oaks | Solar | PV | No | Solar |  | 4.9997 | LV | England | South East | RH149AZ |  | 509003.0 | 130058.0 | 2016
Toucan Energy Services | Ford | Solar | PV | No | Solar |  | 11.5699 | LV | England | South East | BN443AT |  | 517748.0 | 117195.0 | 2016
Toucan Energy Services | Garvinack | Solar | PV | No | Solar |  | 9.6228 | LV | England | South West | TR49EP |  | 177775.0 | 47586.0 | 2015
Toucan Energy Services | Grange Farm | Solar | PV | No | Solar |  | 21.0984 | LV | England | South West | BS361RR |  | 363968.0 | 182366.0 | 2014
Toucan Energy Services | Great Seabrook | Solar | PV | No | Solar |  | 4.965 | LV | England | South East | LU79DY |  | 493192.0 | 217705.0 | 2015
Toucan Energy Services | Guston | Solar | PV | No | Solar |  | 4.9993 | LV | England | South East | CT155EW |  | 632877.0 | 144096.0 | 2015
Toucan Energy Services | Hendai | Solar | PV | No | Solar |  | 13.3954 | LV | Wales | Wales |  | CF828FU | 312392.0 | 197842.0 | 2015
Toucan Energy Services | Hendre Fawr | Solar | PV | No | Solar |  | 11.6259 | LV | Wales | Wales | CF449RJ |  | 291347.0 | 206062.0 | 2015
Toucan Energy Services | Home Farm | Solar | PV | No | Solar |  | 4.9873 | LV | England | South West | GL519RS |  | 393986.0 | 226037.0 | 2017
Toucan Energy Services | Hunciecroft | Solar | PV | No | Solar |  | 7.619 | LV | England | East Midlands | S803ND |  | 454513.0 | 373909.0 | 2015
Toucan Energy Services | Isle of Wight | Solar | PV | No | Solar |  | 6.2264 | LV | England | South East | PO334RW |  | 452614.0 | 90511.0 | 2015
Toucan Energy Services | Lisburn | Solar | PV | No | Solar |  | 20.5 | LV | Northern Ireland | Northern Ireland | BT282SL |  | 134798.0 | 521384.0 | 2017
Toucan Energy Services | Littlewood | Solar | PV | No | Solar |  | 13.728 | LV | England | South East | MK197NF |  | 482105.0 | 247071.0 | 2015
Toucan Energy Services | Malmaynes | Solar | PV | No | Solar |  | 14.8262 | LV | England | South East | ME39SQ |  | 580664.0 | 175335.0 | 2015
Toucan Energy Services | Mill Farm | Solar | PV | No | Solar |  | 4.9967 | LV | England | East Midlands | NG335DP |  | 494872.0 | 331696.0 | 2016
Toucan Energy Services | Moor House | Solar | PV | No | Solar |  | 4.9156 | LV | England | North West | CA144JZ |  | 301300.0 | 525369.0 | 2016
Toucan Energy Services | Morton Solar | Solar | PV | No | Solar |  | 28.0954 | LV | England | East Midlands | DN228HD |  | 467120.0 | 379462.0 | 2015
Toucan Energy Services | New Stone House | Solar | PV | No | Solar |  | 11.4768 | LV | England | South East | OX252PT |  | 455811.0 | 219330.0 | 2015
Toucan Energy Services | Newton | Solar | PV | No | Solar |  | 4.9873 | LV | England | Eastern | NR148GD |  | 624152.0 | 306192.0 | 2016
Toucan Energy Services | Otherton | Solar | PV | No | Solar |  | 2.5186 | LV | England | West Midlands | WR65LS |  | 380432.0 | 254242.0 | 2017
Toucan Energy Services | Outwood | Solar | PV | No | Solar |  | 4.9701 | LV | England | Eastern | CM112TX |  | 568931.0 | 193607.0 | 2016
Toucan Energy Services | Place Farm | Solar | PV | No | Solar |  | 6.7917 | LV | England | South East | TN262LX |  | 597181.0 | 132855.0 | 2015
Toucan Energy Services | Rhydypandy | Solar | PV | No | Solar |  | 6.3801 | LV | Wales | Wales | SA66NX |  | 265957.0 | 200658.0 | 2015
Toucan Energy Services | Rolls Royce | Solar | PV | No | Solar |  | 3.2 | LV | England | South West | BS346QA |  | 360460.0 | 180792.0 | 2016
Toucan Energy Services | Shuttleworth | Solar | PV | No | Solar |  | 4.9991 | LV | England | North West | BB74LL |  | 382296.0 | 448048.0 | 2016
Toucan Energy Services | Stowbridge | Solar | PV | No | Solar |  | 24.323 | LV | England | Eastern | CB63LF |  | 551252.0 | 272416.0 | 2014
Toucan Energy Services | Swindon | Solar | PV | No | Solar |  | 60.8926 | LV | England | South West | SN49NS |  | 413029.0 | 179126.0 | 2016
Toucan Energy Services | Tower Hayes | Solar | PV | No | Solar |  | 4.9991 | LV | England | East Midlands | LE671FH |  | 444576.0 | 310822.0 | 2016
Toucan Energy Services | Trowle | Solar | PV | No | Solar |  | 4.9986 | LV | England | South West | BA149BR |  | 383857.0 | 158625.0 | 2016
Toucan Energy Services | Upper Farm | Solar | PV | No | Solar |  | 10.0105 | LV | England | South East | SO249RY |  | 463453.0 | 141758.0 | 2015
Toucan Energy Services | Upper Wick | Solar | PV | No | Solar |  | 4.9986 | LV | England | South West | GL116DE |  | 371550.0 | 195850.0 | 2015
Toucan Energy Services | Welbeck | Solar | PV | No | Solar |  | 16.0384 | LV | England | East Midlands | NG229EY |  | 460619.0 | 372696.0 | 2015
Toucan Energy Services | Weston Longville | Solar | PV | No | Solar |  | 7.5686 | LV | England | Eastern |  | NR95JF | 610220.0 | 315069.0 | 2015
Toucan Energy Services | Widehurst | Solar | PV | No | Solar |  | 4.9862 | LV | England | South East | TN129LN |  | 575536.0 | 142994.0 | 2017
Toucan Energy Services | Wilbees | Solar | PV | No | Solar |  | 4.9987 | LV | England | South East | BN266RU |  | 554339.0 | 106829.0 | 2016
Toucan Energy Services | Winnards | Solar | PV | No | Solar |  | 4.4528 | LV | England | South West | TR96DG |  | 192864.0 | 66586.0 | 2015
Toucan Energy Services | Woodhouse | Solar | PV | No | Solar |  | 4.9795 | LV | England | West Midlands | ST145HY |  | 409432.0 | 339052.0 | 2017
Toucan Energy Services | Wrea Green | Solar | PV | No | Solar |  | 4.8797 | LV | England | North West | PR42WP |  | 338850.0 | 431150.0 | 2017
UK Transition Limited | West Burton CCGT | Fossil Fuel | CCGT | No | Natural Gas |  | 1332 | HV | England | East Midlands | DN229BL |  | 479368.0 | 384538.0 | 2013
Uniper UK | Connahs Quay | Fossil Fuel | CCGT | No | Sour Gas |  | 1380 | HV | Wales | Wales | CH54BP |  | 328878.0 | 368331.0 | 1996
Uniper UK | Cottam Development Centre | Fossil Fuel | CCGT | No | Natural Gas |  | 445 | HV | England | East Midlands | DN220TF |  | 470307.0 | 378332.0 | 1998
Uniper UK | Enfield | Fossil Fuel | CCGT | No | Natural Gas |  | 408 | HV | England | London | EN37PL |  | 532446.0 | 190691.0 | 1999
Uniper UK | Grain | Fossil Fuel | CCGT | Yes | Natural Gas |  | 1365 | HV | England | South East | ME30AR |  | 588672.0 | 172826.0 | 2011
Uniper UK | Grain (OCGT) | Fossil Fuel | Single cycle | No | Diesel/Gas Oil |  | 50 | HV | England | South East | ME30AR |  | 0.0 | 0.0 | 2011
Uniper UK | Killingholme | Fossil Fuel | Single cycle | No | Natural Gas |  | 600 | HV | England | Yorkshire and Humber | DN403LU |  | 516717.0 | 419816.0 | 1992
Uniper UK | Ratcliffe (OCGT) | Fossil Fuel | Single cycle | No | Diesel/Gas Oil |  | 34 | HV | England | East Midlands | NG110EE |  | 449969.0 | 327738.0 | 1967
Uniper UK | Ratcliffe (Steam) | Fossil Fuel | Conventional steam | No | Coal |  | 2021 | HV | England | East Midlands | NG110EE |  | 449969.0 | 327738.0 | 1967
Uniper UK | Taylors Lane | Fossil Fuel | Single cycle | No | Diesel/Gas Oil |  | 132 | HV | England | London | NW108JP |  | 524680.0 | 195111.0 | 1979
Vattenfall | Aberdeen | Wind | Offshore | No | Wind |  | 96.8 | HV | Scotland | Scotland |  |  | 395748.0 | 814283.0 | 2018
Vattenfall | Clashindarroch | Wind | Onshore | No | Wind |  | 36.9 | HV | Scotland | Scotland |  |  | 348214.0 | 839951.0 | 2015
Vattenfall | Edinbane | Wind | Onshore | No | Wind |  | 41.4 | HV | Scotland | Scotland |  |  | 134353.0 | 850769.0 | 2009
Vattenfall | Kentish Flats | Wind | Offshore | No | Wind |  | 90 | LV | England | South East |  |  | 615015.0 | 178055.0 | 2005
Vattenfall | Kentish Flats Extension | Wind | Offshore | No | Wind |  | 49.5 | LV | England | South East |  |  | 615377.0 | 175526.0 | 2015
Vattenfall | Ormonde | Wind | Offshore | No | Wind |  | 150 | HV | England | North West |  |  | 306000.0 | 466842.0 | 2011
Vattenfall | Pen Y Cymoedd | Wind | Onshore | No | Wind |  | 228 | HV | Wales | Wales |  |  | 292879.0 | 199365.0 | 2016
Vattenfall | Ray | Wind | Onshore | No | Wind |  | 54.4 | LV | England | North East |  |  | 395550.0 | 587550.0 | 2017
Vattenfall | Swinford | Wind | Onshore | No | Wind |  | 22 | LV | England | East Midlands |  |  | 456804.0 | 279647.0 | 2012
Vattenfall | Thanet | Wind | Offshore | No | Wind |  | 300 | HV | England | South East |  |  | 652658.0 | 176367.0 | 2010
Venitent Energy Services | A'Chruach | Wind | Onshore | No | Wind |  | 42.6 | HV | Scotland | Scotland | PA318BA |  | 197742.0 | 696597.0 | 2016
Venitent Energy Services | Ardrossan | Wind | Onshore | No | Wind |  | 30 | LV | Scotland | Scotland | KA227NU |  | 223500.0 | 642500.0 | 2004
Venitent Energy Services | Bears Down | Wind | Onshore | No | Wind |  | 9.6 | LV | England | South West | TR84RJ |  | 190360.0 | 67560.0 | 2001
Venitent Energy Services | Beinn Ghlas | Wind | Onshore | No | Wind |  | 8.4 | LV | Scotland | Scotland | PA351HY |  | 196500.0 | 726000.0 | 1999
Venitent Energy Services | Blackstone Edge | Wind | Onshore | No | Wind |  | 7.5 | LV | England | Yorkshire and Humber | S369PA |  | 419565.0 | 405226.0 | 2013
Venitent Energy Services | Bryn Titli | Wind | Onshore | No | Wind |  | 9.9 | LV | Wales | Wales | SY186RX |  | 293500.0 | 275500.0 | 1994
Venitent Energy Services | Carno | Wind | Onshore | No | Wind |  | 33.6 | LV | Wales | Wales | SY175JT |  | 291053.0 | 295836.0 | 1996
Venitent Energy Services | Causeymire | Wind | Onshore | No | Wind |  | 48.3 | HV | Scotland | Scotland | KW15XR |  | 312000.0 | 950000.0 | 2005
Venitent Energy Services | Dalswinton | Wind | Onshore | No | Wind |  | 30 | HV | Scotland | Scotland | DG20YB |  | 295000.0 | 589000.0 | 2008
Venitent Energy Services | Farr | Wind | Onshore | No | Wind |  | 92 | HV | Scotland | Scotland | IV137ZA |  | 273500.0 | 829000.0 | 2006
Venitent Energy Services | Ffynnon Oer | Wind | Onshore | No | Wind |  | 32 | LV | Wales | Wales | SA133LG |  | 285500.0 | 205500.0 | 2006
Venitent Energy Services | Galawhistle | Wind | Onshore | No | Wind |  | 66 | HV | Scotland | Scotland | ML110SJ |  | 275443.0 | 629080.0 | 2017
Venitent Energy Services | Glenkerie | Wind | Onshore | No | Wind |  | 22 | LV | Scotland | Scotland | ML126QL |  | 310453.0 | 628117.0 | 2012
Venitent Energy Services | Gordonstown Hill | Wind | Onshore | No | Wind |  | 12.5 | LV | Scotland | Scotland | AB538LH |  | 371136.0 | 841396.0 | 2013
Venitent Energy Services | Hill of Fiddes | Wind | Onshore | No | Wind |  | 6.9 | LV | Scotland | Scotland | AB416QR |  | 393495.0 | 824485.0 | 2010
Venitent Energy Services | Kirkby Moor | Wind | Onshore | No | Wind |  | 4.8 | LV | England | North West | LA177UN |  | 326111.0 | 485242.0 | 1993
Venitent Energy Services | Lambrigg | Wind | Onshore | No | Wind |  | 6.5 | LV | England | North West | LA80AP |  | 358800.0 | 493600.0 | 2000
Venitent Energy Services | Lissett Airfield | Wind | Onshore | No | Wind |  | 30 | LV | England | Yorkshire and Humber | YO258PZ |  | 512263.0 | 458139.0 | 2009
Venitent Energy Services | Llyn Alaw | Wind | Onshore | No | Wind |  | 20.4 | LV | Wales | Wales | LL680TB |  | 236000.0 | 387000.0 | 1997
Venitent Energy Services | Low Spinney | Wind | Onshore | No | Wind |  | 8.2 | LV | England | East Midlands | LE175NB |  | 455816.0 | 289705.0 | 2011
Venitent Energy Services | Minsca | Wind | Onshore | No | Wind |  | 36.8 | HV | Scotland | Scotland | DG112QE |  | 313821.0 | 581690.0 | 2008
Venitent Energy Services | Mynydd Clogau | Wind | Onshore | No | Wind |  | 14.45 | LV | Wales | Wales | SY163DQ |  | 303300.0 | 298800.0 | 2006
Venitent Energy Services | Mynydd Gorddu | Wind | Onshore | No | Wind |  | 10.2 | LV | Wales | Wales | SY245DP |  | 266200.0 | 287200.0 | 1998
Venitent Energy Services | North Steads | Wind | Onshore | No | Wind |  | 18.45 | LV | England | North East | NE615BB |  | 425478.0 | 597629.0 | 2016
Venitent Energy Services | Novar | Wind | Onshore | No | Wind |  | 17 | LV | Scotland | Scotland | IV170XJ |  | 255500.0 | 871000.0 | 1997
Venitent Energy Services | Rheidol | Wind | Onshore | No | Wind |  | 2.4 | LV | Wales | Wales | SY233N |  | 272400.0 | 280500.0 | 1997
Venitent Energy Services | Seamer | Wind | Onshore | No | Wind |  | 10.25 | LV | England | North East | TS159JH |  | 448125.0 | 511235.0 | 2012
Venitent Energy Services | Sisters | Wind | Onshore | No | Wind |  | 8.2 | LV | England | North East | NE615ED |  | 425476.0 | 595602.0 | 2016
Venitent Energy Services | Taff Ely | Wind | Onshore | No | Wind |  | 9 | LV | Wales | Wales | CF398DJ |  | 297000.0 | 186000.0 | 1993
Venitent Energy Services | Tedder Hill | Wind | Onshore | No | Wind |  | 7.5 | LV | England | Yorkshire and Humber | HU192BY |  | 530221.0 | 430242.0 | 2013
Venitent Energy Services | Tow Law | Wind | Onshore | No | Wind |  | 2.31 | LV | England | North East | DL134DE |  | 411500.0 | 541000.0 | 2001
Venitent Energy Services | Trysglwyn | Wind | Onshore | No | Wind |  | 5.6 | LV | Wales | Wales | LL689RF |  | 244000.0 | 389000.0 | 1996
Venitent Energy Services | Westfield | Wind | Onshore | No | Wind |  | 10 | LV | Scotland | Scotland | KY50HJ |  | 319640.0 | 695487.0 | 2013
Venitent Energy Services | Wingates | Wind | Onshore | No | Wind |  | 15 | LV | England | North East | NE658RW |  | 413034.0 | 597920.0 | 2013
Veolia | SELCHP | Bioenergy | Bioenergy | Yes | MSW |  | 35 | LV | England | London |  |  | 535605.0 | 178129.0 | 1994
Viridor Waste Management | Runcorn EfW | Bioenergy | Bioenergy | No | MSW |  | 91 | LV | England | North West |  |  | 349985.0 | 381240.0 | 2014
Vitol | Blackburn | Fossil Fuel | CCGT | No | Natural Gas |  | 60 | LV | England | London | BB25HX |  | 364659.0 | 424755.0 | 2002
Vitol | Damhead Creek | Fossil Fuel | CCGT | No | Natural Gas |  | 805 | HV | England | South East | ME39TX |  | 581973.0 | 173211.0 | 2000
Vitol | Rye House | Fossil Fuel | CCGT | No | Natural Gas |  | 715 | HV | England | Eastern | EN110RF |  | 538365.0 | 209811.0 | 1993
Vitol | Shoreham | Fossil Fuel | CCGT | No | Natural Gas |  | 420 | LV | England | South East | BN411WF |  | 521488.0 | 105110.0 | 2000
Vitol | VPI | Fossil Fuel | CCGT | Yes | Natural Gas |  | 1268 | HV | England | Yorkshire and Humber | DN403DZ |  | 518189.0 | 412390.0 | 2004
Wise Energy Limited | Blenches Mill Solar Park | Solar | PV | No | Solar |  | 6.0788 | LV | England | South West |  |  | 386848.0 | 152850.0 | 2014
Wise Energy Limited | Burcroft Solar Parks | Solar | PV | No | Solar |  | 12.669 | LV | England | South West |  |  | 300442.0 | 97423.0 | 2014
Wise Energy Limited | Chilton Cantelo Solar park | Solar | PV | No | Solar |  | 4.997 | LV | England | South West |  |  | 357797.0 | 121851.0 | 2012
Wise Energy Limited | Crossways Solar Park | Solar | PV | No | Solar |  | 4.997 | LV | England | South West |  |  | 377476.0 | 88548.0 | 2012
Wise Energy Limited | Hook Valley Solar Park | Solar | PV | No | Solar |  | 15.3 | LV | England | Eastern |  |  | 610859.0 | 251069.0 | 2014
Wise Energy Limited | Knockworthy Farm Solar Park | Solar | PV | No | Solar |  | 4.6452 | LV | England | South West |  |  | 251121.0 | 122799.0 | 2013
Wise Energy Limited | Raglington Farm Solar Park | Solar | PV | No | Solar |  | 5.733 | LV | England | South East |  |  | 454062.0 | 113445.0 | 2013
Wise Energy Limited | Whitley (Ashcott Farm) Solar Park | Solar | PV | No | Solar |  | 7.5702 | LV | England | South West |  |  | 344449.0 | 137081.0 | 2014
Wise Energy Limited | Wyld Meadow Farm Solar Park | Solar | PV | No | Solar |  | 4.8384 | LV | England | South West |  |  | 334144.0 | 98155.0 | 2012
WPO UK Services | Airies | Wind | Onshore | No | Wind |  | 39.9 | HV | Scotland | Scotland |  | NX2662767127 | 226000.0 | 568000.0 | 2017
WPO UK Services | Altaveedan | Wind | Onshore | No | Wind |  | 18 | HV | Northern Ireland | Northern Ireland |  | NW2793786653 | 126801.0 | 584314.0 | 2016
WPO UK Services | AOE | Wind | Onshore | No | Wind |  | 11.5 | HV | Scotland | Scotland |  | NS5802548945 | 257717.0 | 648148.0 | 2014
WPO UK Services | Asfordby A | Solar | PV | No | Solar |  | 4.91 | LV | England | East Midlands |  | SK7184120877 |  |  | 2016
WPO UK Services | Asfordby B | Solar | PV | No | Solar |  | 4.98 | LV | England | East Midlands |  | SK7184120877 |  |  | 2016
WPO UK Services | Ashby | Solar | PV | No | Solar |  | 4.7991 | LV | England | East Midlands |  | SK3432917585 | 434525.0 | 317774.0 | 2016
WPO UK Services | Bake Farm | Solar | PV | No | Solar |  | 4.9993 | LV | England | South West |  | SX3264958430 | 233036 | 58842 | 2015
WPO UK Services | Betty Hill | Wind | Onshore | No | Wind |  | 6 | HV | Scotland | Scotland |  | NC7286961774 | 272326 | 962920 | 2013
WPO UK Services | Box Road | Solar | PV | No | Solar |  | 1.903 | LV | England | South West |  | SO7520502233 |  |  | 2016
WPO UK Services | Burton Wold | Wind | Onshore | No | Wind |  | 20 |  | England | East Midlands |  | SP 91204 74882 |  |  | 2006
WPO UK Services | Caergarw | Solar | PV | No | Solar |  | 4.934 | LV | Wales | Wales |  | SS8105383495 |  |  | 2017
WPO UK Services | Caldecote | Solar | PV | No | Solar |  | 4.977 | LV | England | Eastern |  | TL2072157273 |  |  | 2016
WPO UK Services | Clapham | Solar | PV | No | Solar |  | 4.98 | LV | England | Eastern |  | TL0371454289 |  |  | 2015
WPO UK Services | Combermere | Solar | PV | No | Solar |  | 13.97 | LV | England | North West |  | SJ6003644925 |  |  | 2015
WPO UK Services | Crumlin | Solar | PV | No | Solar |  | 4.55 | LV | Wales | Wales |  | ST2032097981 |  |  | 2016
WPO UK Services | Dummuies | Wind | Onshore | No | Wind |  | 12.25 | LV | Scotland | Scotland |  | NJ5635836050 |  |  | 2007
WPO UK Services | Eye | Wind | Onshore | No | Wind |  | 5 | HV | England | Eastern |  | TM1308575398 | 613107 | 275558 | 2013
WPO UK Services | Far Danes | Solar | PV | No | Solar |  | 11.7 | LV | England | East Midlands |  | SK8642581821 |  |  | 2016
WPO UK Services | FMC Dunfermline | Wind | Onshore | No | Wind |  | 1.5 | HV | Scotland | Scotland |  | NT1017885549 | 310010 | 685787 | 2012
WPO UK Services | Garves | Wind | Onshore | No | Wind |  | 15 |  | Northern Ireland | Northern Ireland |  | NW 15696 78785 |  |  | 2009
WPO UK Services | Grange | Solar | PV | No | Solar |  | 14 | LV | England | East Midlands |  | TF3932618855 | 545055 | 318754 | 2013
WPO UK Services | Greenvale March | Wind | Onshore | No | Wind |  | 1.5 | HV | England | Eastern |  | TL3551493287 | 535656 | 293166 | 2014
WPO UK Services | Haverigg III | Wind | Onshore | No | Wind |  | 3.4 | HV | England | North West |  | SD1393279392 | 313300 | 479100 | 2005
WPO UK Services | Kelly Green | Solar | PV | No | Solar |  | 4.98 | LV | England | South West |  | SX0496075550 |  |  | 2016
WPO UK Services | Kirton | Solar | PV | No | Solar |  | 3.51 | LV | England | East Midlands |  | TF2760238140 |  |  | 2016
WPO UK Services | Lains Farm | Solar | PV | No | Solar |  | 4.54 | LV | England | South East |  | SU2792344625 |  |  | 2016
WPO UK Services | Lairg | Wind | Onshore | No | Wind |  | 7.5 | LV | Scotland | Scotland |  | NC6098003860 | 261293 | 903916 | 2012
WPO UK Services | Magazine | Solar | PV | No | Solar |  | 3.449 | LV | England | West Midlands |  | SP2837497084 |  |  | 2017
WPO UK Services | Milton Keynes | Wind | Onshore | No | Wind |  | 14 |  | England | East Midlands |  | SP 90513 49351 |  |  | 2010
WPO UK Services | Moor Farm | Solar | PV | No | Solar |  | 3.73 | LV | England | West Midlands |  | SJ4168023332 |  |  | 2017
WPO UK Services | Nailstone | Solar | PV | No | Solar |  | 4.9755 | LV | England | East Midlands |  | SK4312408016 |  |  | 2017
WPO UK Services | Newnham | Solar | PV | No | Solar |  | 11.638 | LV | England | South West |  | SX5607658771 |  |  | 2015
WPO UK Services | Ora More | Wind | Onshore | No | Wind |  | 15 |  | Northern Ireland | Northern Ireland |  | NV 17675 09223 |  |  | 2017
WPO UK Services | Pates Hill | Wind | Onshore | No | Wind |  | 14 |  | Scotland | Scotland |  | NT 00099 59791 |  |  | 2010
WPO UK Services | PoL | Wind | Onshore | No | Wind |  | 10 | HV | England | North West |  | SJ3303294659 | 333356 | 395230 | 2008
WPO UK Services | Quixwood Moor | Wind | Onshore | No | Wind |  | 26.65 |  | Scotland | Scotland |  | NT 76067 64408 |  |  | 2017
WPO UK Services | Robert's Wall | Solar | PV | No | Solar |  | 2.56 | LV | Wales | Wales |  | SN1001400495 |  |  | 2015
WPO UK Services | Rosedew | Solar | PV | No | Solar |  | 4.98 | LV | Wales | Wales |  | SS9126567595 |  |  | 2016
WPO UK Services | Slieve Rushen | Wind | Onshore | No | Wind |  | 54 |  | Northern Ireland | Northern Ireland |  | SA 37620 86730 |  |  | 2008
WPO UK Services | Somersall | Solar | PV | No | Solar |  | 2.56 | LV | England | East Midlands |  | SK1320934074 |  |  | 2015
WPO UK Services | Twin Rivers | Wind | Onshore | No | Wind |  | 28.7 |  | England | East Midlands |  | SE 79584 35504 |  |  | 2016
WPO UK Services | Winscales Moor | Wind | Onshore | No | Wind |  | 5.95 |  | England | North West |  | NY 03390 26409 |  |  | 2009
XceCo | Inner Dowsing Wind Farm | Wind | Offshore | No | Wind |  | 97.2 | HV | England | East Midlands |  | TF536655 | 563561 | 368447 | 2008
XceCo | Lynn Wind Farm | Wind | Offshore | No | Wind |  | 97.2 | HV | England | East Midlands |  | TF536655 | 564095 | 362638 | 2008

## Stats DUKES 5.11
Pivot Table analysis of DUKES 5.11 - List of major power produces in the UK
Secondary Fuel | (All)
CHP | (All)
Row Labels | Average of InstalledCapacity (MW) | Count of InstalledCapacity (MW) | StdDev of InstalledCapacity (MW) | Sum of InstalledCapacity (MW)
Biomass | 281.716 | 12 | 751.1517 | 3380.592
Coal | 1290 | 2 | 1033.7901 | 2580
Diesel/Gas Oil | 56.4316 | 19 | 53.985 | 1072.2
Natural Gas | 704.9784 | 43 | 519.9306 | 30314.07
Grand Total | 491.4061 | 76 | 589.2462 | 37346.862

## final_figures
Estimations of plant capacity
Cells highlighted in this colour are the values estimated from DUKES 5.11 - May 2023 data | [8 empty] | Final Figures
Site Name | Fuel | Year | Total Generation Capacity (GW) | Estimated Capacity (GW) | Nox (g/kWh) | Nox (mg/kWh) | Source | Notes | Fuel | Year | Capacity (GW) | Nox (g/kWh) | Nox (mg/kWh)
Drax | Biomass | 2022 | 2.6 | 2.6 | 0.47115 | 471.1473 | https://www.drax.com/wp-content/uploads/2023/03/Drax_ESG2022_Single_Pages.pdf | Assumption made that proportion of Biomass to Hydro power same in 2021 and 2022 | Biomass | 2022 | 3.1 | 0.47115 | 471.1473
Drax | Coal | 2022 | 1.4 | 1.4 | 1.1 | 1100 | https://www.drax.com/wp-content/uploads/2023/03/Drax_ESG2022_Single_Pages.pdf | [note 1]
Drax | Biomass | 2021 | 2.6 | 2.6 | 0.46818 | 468.1824 | https://www.drax.com/wp-content/uploads/2023/03/Drax_ESG2022_Single_Pages.pdf |  | Biomass | 2021 | 3.1 | 0.46818 | 468.1824
Drax | Coal | 2021 | 1.4 | 1.4 | 0.48545 | 485.4545 | https://www.drax.com/wp-content/uploads/2023/03/Drax_ESG2022_Single_Pages.pdf |  | Coal | 2021 | 1.4 | 0.48545 | 485.4545
Uniper Europe | Gas and Coal | 2022 | 14.8 | 1 | 0.32782 | 327.8237 | https://www.uniper.energy/system/files/2023-04/2023-04-06_FY_2022_Uniper_Sustainability_Report_.pdf | Taking an average of both the Gas and Coal fired stations from sheet Stats DUKES 5.11 e.g. 1290 + 705 | Gas and Coal | 2022 | 1 | 0.32782 | 327.8237
RWE Total | Lignite | 2022 | 7.6 | N/A | 0.73 | 730 | https://www.rwe.com/-/media/RWE/documents/09-verantwortung-nachhaltigkeit/cr-berichte/sustainability-performance-report-2022.pdf | Leaving as no lignite only plants specified in UK
RWE Total | Hard Coal | 2022 | 1.5 | 1.3 | 0.35 | 350 | https://www.rwe.com/-/media/RWE/documents/09-verantwortung-nachhaltigkeit/cr-berichte/sustainability-performance-report-2022.pdf | Taking 1.3 GW value (1290 MW to 2sf) | Hard Coal | 2022 | 1.3 | 0.35 | 350
RWE Total | Gas | 2022 | 14.3 | 0.7 | 0.14 | 140 | https://www.rwe.com/-/media/RWE/documents/09-verantwortung-nachhaltigkeit/cr-berichte/sustainability-performance-report-2022.pdf | Taking 0.7 GW value (704 MW to 2sf) | Gas | 2022 | 0.7 | 0.14 | 140
RWE Total | Lignite | 2021 | 8.5 | N/A | 0.78 | 780 | https://www.rwe.com/-/media/RWE/documents/09-verantwortung-nachhaltigkeit/cr-berichte/sustainability-performance-report-2022.pdf | Leaving as no lignite only plants specified in UK
RWE Total | Hard Coal | 2021 | 1.5 | 1.3 | 0.37 | 370 | https://www.rwe.com/-/media/RWE/documents/09-verantwortung-nachhaltigkeit/cr-berichte/sustainability-performance-report-2022.pdf | Taking 1.3 GW value (1290 MW to 2sf) | Hard Coal | 2021 | 1.3 | 0.37 | 370
RWE Total | Gas | 2021 | 14.3 | 0.7 | 0.15 | 150 | https://www.rwe.com/-/media/RWE/documents/09-verantwortung-nachhaltigkeit/cr-berichte/sustainability-performance-report-2022.pdf | Taking 0.7 GW value (704 MW to 2sf) | Gas | 2021 | 0.7 | 0.15 | 150
[note 1] - This case has been removed from the final dataset on account of the low generation, indicating short operating hours which may not have been subjetc to emission regulations

## from_EMEPEEA
Source[1] | Fuel type [2] | New or existing plant [3] |  | Boiler size or technology, MWth | Reference O2 content, %v/v dry | AEL or ELV concentration, mg N02.m-3 at STP (0°C, 101.3kPa) dry at reference O2 content |  | Emission factor [4], g•GJ-1 (net thermal input)
Notes : 1) BREF denotes the large combustion plant BAT reference document, LCPD denotes Directive 2001/80/EC, Goburg denotes the Gothenburg protocol of 1999. 2) Fuel is main classification only, limits may be for ‘solid fuels’ rather than coal or wood. Limits for gaseous fuels are for natural gas and may not be applicable to derived or other gaseous fuels. 3) Note that new and existing plant have specific meanings under LCPD. 4) Emission factors calculated from emission concentrations using USEPA methodology (See Appendix E for details).
|  |  | Min | Max |  | Low | High | Low | High
BREF | coal | new | 50 | 100 | 6 | 90 | 300 | 32.6 | 108.7
BREF | coal | new | 100 | 300 | 6 | 90 | 200 | 32.6 | 72.5
BREF | coal | new | 300 |  | 6 | 50 | 150 | 18.1 | 54.3
LCPD | coal | new | 50 | 500 | 6 | 600 |  | 217.4
LCPD | coal | new | 500 |  | 6 | 500 |  | 181.1
LCPD | coal | New 2016 | 500 |  | 6 | 200 |  | 72.5
Goburg | coal | new | 50 | 100 | 6 | 400 |  | 144.9
Goburg | coal | new | 100 | 300 | 6 | 300 |  | 108.7
Goburg | coal | new | 300 |  | 6 | 200 |  | 72.5
BREF | coal | existing | 50 | 100 | 6 | 90 | 300 | 32.6 | 108.7
BREF | coal | existing | 100 | 300 | 6 | 90 | 200 | 32.6 | 72.5
BREF | coal | existing | 300 |  | 6 | 50 | 200 | 18.1 | 72.5
LCPD | coal | existing | 50 | 500 | 6 | 600 |  | 217.4
LCPD | coal | existing | 500 |  | 6 | 500 |  | 181.1
LCPD | coal | EX. 2016 |  | 500 | 6 | 200 |  | 72.5
Goburg | coal | existing | 50 |  | 6 | 650 |  | 235.5
BREF | wood | new | 50 | 100 | 6 | 150 | 250 | 57.9 | 96.4
BREF | wood | new | 100 | 300 | 6 | 150 | 200 | 57.9 | 77.1
BREF | wood | new | 300 |  | 6 | 50 | 150 | 19.3 | 57.9
LCPD | wood | new | 50 | 100 | 6 | 400 |  | 154.3
LCPD | wood | new | 100 | 500 | 6 | 300 |  | 115.7
LCPD | wood | new | 500 |  | 6 | 200 |  | 77.1
Goburg | wood | new | 50 | 100 | 6 | 400 |  | 154.3
Goburg | wood | new | 100 | 300 | 6 | 300 |  | 115.7
Goburg | wood | new | 300 |  | 6 | 200 |  | 77.1 |  | https://www.eea.europa.eu/publications/emep-eea-guidebook-2019/part-b-sectoral-guidance-chapters/1-energy/1-a-combustion/1-a-1-energy-industries/view
BREF | wood | existing | 50 | 100 | 6 | 150 | 300 | 57.9 | 115.7
BREF | wood | existing | 100 | 300 | 6 | 150 | 250 | 57.9 | 96.4
BREF | wood | existing | 300 | 300 | 6 | 50 | 200 | 19.3 | 77.1
Goburg | wood | existing | 50 |  | 6 | 650 |  | 250.7
BREF | oil | new | 50 | 100 | 3 | 150 | 300 | 42.4 | 84.9
BREF | oil | new | 100 | 300 | 3 | 50 | 150 | 14.1 | 42.4
BREF | oil | new | 300 |  | 3 | 50 | 100 | 14.1 | 28.3
LCPD | oil | new | 50 | 100 | 3 | 400 |  | 113.2
LCPD | oil | new | 100 | 300 | 3 | 200 |  | 56.6
LCPD | oil | new | 300 |  | 3 | 200 |  | 56.6
Goburg | oil | new | 50 | 100 | 3 | 400 |  | 113.2
Goburg | oil | new | 100 | 300 | 3 | 300 |  | 84.9
Goburg | oil | new | 300 |  | 3 | 200 |  | 56.6
BREF | oil | existing | 50 | 100 | 3 | 150 | 450 | 42.4 | 127.3
BREF | oil | existing | 100 | 300 | 3 | 50 | 200 | 14.1 | 56.6
BREF | oil | existing | 300 |  | 3 | 50 | 150 | 14.1 | 42.4
LCPD | oil | existing | 50 | 500 | 3 | 450 |  | 127.3
LCPD | oil | existing | 500 |  | 3 | 400 |  | 113.2
Goburg | oil | existing | 50 |  | 3 | 450 |  | 127.3
BREF | gas | new | 50 | 50 | 3 | 50 | 100 | 14.2 | 28.3
LCPD | gas | new | 50 | 300 | 3 | 150 |  | 42.5
LCPD | gas | new | 300 |  | 3 | 100 |  | 28.3
Goburg | gas | new | 50 | 300 | 3 | 150 |  | 42.5
Goburg | gas | new | 300 |  | 3 | 100 |  | 28.3
BREF | gas | existing | 50 |  | 3 | 50 | 100 | 14.2 | 28.3
LCPD | gas | existing | 50 | 500 | 3 | 300 |  | 85
LCPD | gas | existing | 500 |  | 3 | 200 |  | 56.6
Goburg | gas | existing | 50 |  | 3 | 350 |  | 99.1

## PM_from_EMEPEEA
Source[1] | Fuel type [2] | New or existing plant [3] |  | Boiler size or technology, MWth | Reference O2 content, %v/v dry | AEL or ELV concentration, mg N02.m-3 at STP (0°C, 101.3kPa) dry at reference O2 content |  | Emission factor [4], g•GJ-1 (net thermal input)
|  |  | Min | Max |  | Low | High | Low | High
BREF | coal | new | 50 | 100 | 6 | 5 | 20 | 1.8 | 7.2
BREF | coal | new | 100 | 300 | 6 | 5 | 20 | 1.8 | 7.2
BREF | coal | new | 300 |  | 6 | 5 | 20 | 1.8 | 7.2
LCPD | coal | new | 50 | 500 | 6 | 100 |  | 36.2
LCPD | coal | new | 500 |  | 6 | 50 |  | 18.1
LCPD | coal | new | 50 | 100 | 6 | 50 |  | 18.1
LCPD | coal | new | 100 |  | 6 | 30 |  | 10.9
BREF | coal | existing | 50 | 100 | 6 | 5 | 30 | 1.8 | 10.9
BREF | coal | existing | 100 | 300 | 6 | 5 | 30 | 1.8 | 10.9
BREF | coal | existing | 300 |  | 6 | 5 | 30 | 1.8 | 10.9
LCPD | coal | existing | 50 | 500 | 6 | 100 |  | 36.2
LCPD | coal | existing | 500 |  | 6 | 50 |  | 18.1
BREF | wood | new | 50 | 100 | 6 | 5 | 20 | 1.9 | 7.7
BREF | wood | new | 100 | 300 | 6 | 5 | 20 | 1.9 | 7.7
BREF | wood | new | 300 |  | 6 | 5 | 20 | 1.9 | 7.7
BREF | wood | existing | 50 | 100 | 6 | 5 | 20 | 1.9 | 7.7
BREF | wood | existing | 100 | 300 | 6 | 5 | 20 | 1.9 | 7.7
BREF | wood | existing | 300 |  | 6 | 5 | 20 | 1.9 | 7.7
BREF | oil | new | 50 | 100 | 3 | 5 | 20 | 1.4 | 5.7
BREF | oil | new | 100 | 300 | 3 | 5 | 20 | 1.4 | 5.7
BREF | oil | new | 300 |  | 3 | 5 | 10 | 1.4 | 2.8
LCPD | oil | new | 50 |  | 3 | 50 |  | 14.1
LCPD | oil | new | 50 | 100 | 6 | 50 |  | 17
LCPD | oil | new | 100 |  | 6 | 30 |  | 10.2
BREF | oil | existing | 50 | 100 | 3 | 5 | 30 | 1.4 | 8.5
BREF | oil | existing | 100 | 300 | 3 | 5 | 25 | 1.4 | 7.1
BREF | oil | existing | 300 |  | 3 | 5 | 20 | 1.4 | 5.7
LCPD | oil | existing | 50 |  | 3 | 50 |  | 14.1
LCPD | gas | new | 50 |  | 3 | 5 |  | 1.4
LCPD | gas | new | 50 |  | 3 | 5 |  | 1.4
LCPD | gas | existing | 50 |  | 3 | 5 |  | 1.4